## Hi-wall
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
WALL-MOUNTED
Indoor unit(s) | : | 42QHF009DS x 4
Outdoor unit | : | 38QUS036DS4
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 10.5 | kW | cooling | SEER | 5.1 | -
heating/Average | Pdesignh | 10.2 | kW | heating/Average | SCOP/A | 3.8 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 10.6 | kW | Tj = 35℃ | EERd | 2.72 | -
Tj = 30℃ | Pdc | 7.379 | kW | Tj = 30℃ | EERd | 4.33 | -
Tj = 25℃ | Pdc | 4.947 | kW | Tj = 25℃ | EERd | 6.33 | -
Tj = 20℃ | Pdc | 2.968 | kW | Tj = 20℃ | EERd | 8.34 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 8.669 | kW | Tj = -7℃ | COPd | 2.36 | -
Tj = 2℃ | Pdh | 5.571 | kW | Tj = 2℃ | COPd | 3.75 | -
Tj = 7℃ | Pdh | 3.714 | kW | Tj = 7℃ | COPd | 5.25 | -
Tj = 12℃ | Pdh | 3.172 | kW | Tj = 12℃ | COPd | 5.62 | -
Tj = bivalent temperature | Pdh | 8.669 | kW | Tj = bivalent temperature | COPd | 2.36 | -
Tj = operating limit | Pdh | 7.191 | kW | Tj = operating limit | COPd | 1.97 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.019 | kW | cooling | QCE | 721 | kWh/a
standby mode | Psb | 0.019 | kW | heating/Average | Qhe | 3758 | kWh/a
thermostat-off mode | Pto | 0.068 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 55/69 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Ducted
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Ducted
Indoor unit(s) | : | 42QSM009DS x 4
Outdoor unit | : | 38QUS036DS4
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 10.5 | kW | cooling | SEER | 5.1 | -
heating/Average | Pdesignh | 10.2 | kW | heating/Average | SCOP/A | 3.8 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 10.5 | kW | Tj = 35℃ | EERd | 2.77 | -
Tj = 30℃ | Pdc | 7.423 | kW | Tj = 30℃ | EERd | 4.41 | -
Tj = 25℃ | Pdc | 4.86 | kW | Tj = 25℃ | EERd | 6.13 | -
Tj = 20℃ | Pdc | 2.69 | kW | Tj = 20℃ | EERd | 9.54 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 9.3 | kW | Tj = -7℃ | COPd | 2.43 | -
Tj = 2℃ | Pdh | 5.815 | kW | Tj = 2℃ | COPd | 3.68 | -
Tj = 7℃ | Pdh | 3.672 | kW | Tj = 7℃ | COPd | 5.25 | -
Tj = 12℃ | Pdh | 3.432 | kW | Tj = 12℃ | COPd | 6.24 | -
Tj = bivalent temperature | Pdh | 9.18 | kW | Tj = bivalent temperature | COPd | 2.43 | -
Tj = operating limit | Pdh | 8.709 | kW | Tj = operating limit | COPd | 2.31 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.016 | kW | cooling | QCE | 721 | kWh/a
standby mode | Psb | 0.016 | kW | heating/Average | Qhe | 3758 | kWh/a
thermostat-off mode | Pto | 0.14 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 55/69 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Cassette
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Cassette
Indoor unit(s) | : | 42QTD009DS x 4
Outdoor unit | : | 38QUS036DS4
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 10.5 | kW | cooling | SEER | 5.1 | -
heating/Average | Pdesignh | 10.2 | kW | heating/Average | SCOP/A | 3.8 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 10.5 | kW | Tj = 35℃ | EERd | 2.77 | -
Tj = 30℃ | Pdc | 7.423 | kW | Tj = 30℃ | EERd | 4.41 | -
Tj = 25℃ | Pdc | 4.86 | kW | Tj = 25℃ | EERd | 6.13 | -
Tj = 20℃ | Pdc | 2.69 | kW | Tj = 20℃ | EERd | 9.54 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 9.3 | kW | Tj = -7℃ | COPd | 2.43 | -
Tj = 2℃ | Pdh | 5.815 | kW | Tj = 2℃ | COPd | 3.68 | -
Tj = 7℃ | Pdh | 3.672 | kW | Tj = 7℃ | COPd | 5.25 | -
Tj = 12℃ | Pdh | 3.432 | kW | Tj = 12℃ | COPd | 6.24 | -
Tj = bivalent temperature | Pdh | 9.18 | kW | Tj = bivalent temperature | COPd | 2.43 | -
Tj = operating limit | Pdh | 8.709 | kW | Tj = operating limit | COPd | 2.31 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.016 | kW | cooling | QCE | 721 | kWh/a
standby mode | Psb | 0.016 | kW | heating/Average | Qhe | 3758 | kWh/a
thermostat-off mode | Pto | 0.14 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 54/69 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Console
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Console
Indoor unit(s) | : | 42QFA009DS x 4
Outdoor unit | : | 38QUS036DS4
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 10.5 | kW | cooling | SEER | 5.1 | -
heating/Average | Pdesignh | 10.2 | kW | heating/Average | SCOP/A | 3.8 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 10.66 | kW | Tj = 35℃ | EERd | 2.2572 | -
Tj = 30℃ | Pdc | 7.486 | kW | Tj = 30℃ | EERd | 4.1985 | -
Tj = 25℃ | Pdc | 5.097 | kW | Tj = 25℃ | EERd | 7.3128 | -
Tj = 20℃ | Pdc | 3.002 | kW | Tj = 20℃ | EERd | 9.5 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 9.333 | kW | Tj = -7℃ | COPd | 2.3444 | -
Tj = 2℃ | Pdh | 5.697 | kW | Tj = 2℃ | COPd | 3.7431 | -
Tj = 7℃ | Pdh | 3.898 | kW | Tj = 7℃ | COPd | 5.1561 | -
Tj = 12℃ | Pdh | 3.12 | kW | Tj = 12℃ | COPd | 5.9203 | -
Tj = bivalent temperature | Pdh | 9.333 | kW | Tj = bivalent temperature | COPd | 2.34 | -
Tj = operating limit | Pdh | 7.336 | kW | Tj = operating limit | COPd | 1.99 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.0195 | kW | cooling | QCE | 721 | kWh/a
standby mode | Psb | 0.0186 | kW | heating/Average | Qhe | 3758 | kWh/a
thermostat-off mode | Pto | 0.0195 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 57/69 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.