## Slide 1: Introduction for Multi Units

## Slide 2
Basic Information
>>
01
Contents
Technical features
>>
02
Difference to old
>>
03

## Slide 3
Part I Basic Information

## Slide 4
Split |  |  |  |  |  | 
Compact Cassette |  |  |  |  |  | 
Super-slim Cassette |  |  |  |  |  | 
Duct |  |  |  |  |  | 
Under Ceiling |  |  |  |  |  | 
Series
7K
9K
12K
24K
Panel
Note: 7K-24K hi-wall units and 12-24K light commercial units are universal for multi and mono connection,36K ODU specially could connect 27K Hydraulic Box, could provide life heat water.
Product line Basic Information
Basic Information Features
Indoor units
18K

## Slide 5
Product line Basic Information
Basic Information Features
Remote controller
IDU | Remote
QHG Model | RG67G(16~30℃）
QHE Model | RG10(16~30℃）with intelligent eye
Compact cassette(7K/9K) Duct(7K/9K) | RG67N (17~30℃）
Compact cassette(12K/18K) Duct(12K/18K/24K) Under Ceiling (18K/24K) | RG67G(16~30℃）
Slim Cassette(24K) | RG67G1(16~30℃）with independent vane

## Slide 6
Product line Basic Information
Basic Information Features
Remote controller
RG67N
(17~30℃）
RG67G
(16~30℃）
RG67G1
(16~30℃）
with independent vane
RG10
(16~30℃）with intelligent eye

## Slide 7
Note: Pdesignc/Pdesignh/SEER/SCOP are tested by combination at capacity ratio 1. Capacity ratio means indoor total capacity is equal to outdoor capacity, for example 7Kx2=14K, 9Kx3=27K.
Product line Basic Information
Outdoor units(For EU R32 Product)
(1 drive 3) 21K, 27K
X4(890x342x673mm)
(1 drive 2) 14K, 18K X3(805x330x554mm)
(1 drive 4) 28K, 36K
(1 drive 5) 42K
D(946×410×810mm)
Basic Information Features

## Slide 8
Product line Basic Information
Installation requirement
Outdoor units | Max. Length |  | Max. Elevation | 
 | Total length | One indoor | Between indoor and outdoor | Between indoor and indoor
1 drive 2 | 40 | 25 | 15 | 10
1 drive 3 | 60 | 30 | 15 | 10
1 drive 4 | 80 | 35 | 15 | 10
1 drive 5 | 80 | 35 | 15 | 10
Basic Information Features

## Slide 9
 | Model | Liquid (mm) | Gas (mm) | Max. length /elevation (m) | Additional gas charge (g/m)
Indoor unit | 7K9K12K | Ф6.35 | Ф9.52 | 25-35/ IDU AND ODU: 15 Between IDUs: 10 | 12
 | 18K | Ф6.35 | Ф12.7 | 25-35/ IDU AND ODU: 15 Between IDUs: 10 | 12
 | 24K | Ф9.52 | Ф15.9 | 35/ IDU AND ODU: 15 Between IDUs: 10 | 24
Outdoor unit | 14K18K (Dual) | Ф6.35 x 2 | Ф9.52 x 2 | Single: 25 Total: 40 | 
 | 21K27K (Triple) | Ф6.35 x 3 | Ф9.52 x 3 | Single: 30 Total: 60 | 
 | 28K36K (quadruple) | Ф6.35 x 4 | Ф9.52 x 3 Ф12.7 x 1 | Single: 35 Total: 80 | 
 | 42K (quintuple) | Ф6.35 x 5 | Ф9.52 x 4 Ф12.7 x 1 | Single: 35 Total: 80 | 
The refrigerant pre-charged inside the outdoor unit is applied to 7.5m standard pipes each.
If the actual pipes are longer than 7.5m, extra refrigerant charging for every liquid pipe is necessary.
Product line Basic Information
Installation requirement
Basic Information Features

## Slide 10
For 14K-27K, all connectors are 6.35/9.52,
When connect 18K IDU, pipe adaptor (Ф9.52 → Ф 12.7) needs to be fixed on the gas valve of outdoor unit.
Product line Basic Information
Installation requirement
Capacity | Joint | Pipe | Dimension |  | Adaptor I (for 18K IDU), Standard
14K | A | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | B | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 3/8→1/2
18K | A | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | B | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 3/8→1/2
21K | A | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | B | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | C | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 3/8→1/2
27K | A | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | B | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 
 | C | Liquid | 1/4 | 6.35 | 
 |  | Gas | 3/8 | 9.52 | 3/8→1/2
Basic Information Features

## Slide 11
Product line Basic Information
Installation requirement
Capacity | Joint | Pipe | Dimension |  | Adaptor I (for 18K IDU), Standard | Adaptor II (for 7-12K IDU), Standard
28K | A | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | B | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | C | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | E | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 1/2 | 12.7 |  | 1/2→3/8
36K | A | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | B | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | C | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | E | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 1/2 | 12.7 |  | 1/2→3/8
42K | A | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | B | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | C | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 |  | 
 | D | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 3/8 | 9.52 | 3/8→1/2 | 
 | E | Liquid | 1/4 | 6.35 |  | 
 |  | Gas | 1/2 | 12.7 |  | 1/2→3/8
For 28K-42K, one connector is 6.35/12.7,
When connect to 7K-12K, pipe adaptor (Ф12.7 → Ф 9.52) needs to be fixed on the gas valve of outdoor unit.
The other connectors are 6.35/9.52, when connect 18K IDU, pipe adaptor (Ф9.52 → Ф 12.7) needs to be fixed on the gas valve of outdoor unit.
Basic Information Features

## Slide 12
Product line Basic Information
Installation requirement
For 28K-42K, the connector 6.35/12.7 cannot connect with 24K indoor unit.
When connect to 24K, two pipe adaptors (Liquid: Ф6.35 → Ф 9.52, Gas: Ф12.7 → Ф 15.9, ) need to be fixed on the valve of outdoor unit.
Basic Information Features

## Slide 13
Product line Basic Information
Installation combination
Maximum combination is 130%
14K
One Unit | Two Unit | 
7 | 7+7 | 9+12
9 | 7+9 | 12+12
12 | 7+12 | 
18 | 9+9 | 
18K
One Unit | Two Unit |  | Three Unit | 
7 | 7+7 | 9+9 | 7+7+7 | 9+9+9
9 | 7+9 | 9+12 | 7+7+9 | 
12 | 7+12 | 9+18 | 7+7+12 | 
18 | 7+18 | 12+12 | 7+9+9 | 
21K
PS : maximum combination is based on not all indoor units will turn on at the same time.
One Unit | Two Unit | 
7 | 7+7 | 9+12
9 | 7+9 | 
12 | 7+12 | 
18 | 9+9 | 
Basic Information Features

## Slide 14
Product line Basic Information
Installation combination
One Unit | Two Unit |  |  | Three Unit |  | 
7 | 7+7 | 9+9 | 12+18 | 7+7+7 | 7+9+12 | 9+12+12
9 | 7+9 | 9+12 |  | 7+7+9 | 7+12+12 | 
12 | 7+12 | 9+18 |  | 7+7+12 | 9+9+9 | 
18 | 7+18 | 12+12 |  | 7+9+9 | 9+9+12 | 
Combination table for 27K
Combination table for 28K
One Unit | Two Unit |  |  | Three Unit |  |  | Four Unit | 
7 | 7+7 | 9+9 | 12+18 | 7+7+7 | 7+9+12 | 9+9+18 | 7+7+7+7 | 7+9+9+9
9 | 7+9 | 9+12 | 12+24 | 7+7+9 | 7+9+18 | 9+12+12 | 7+7+7+9 | 9+9+9+9
12 | 7+12 | 9+18 | 18+18 | 7+7+12 | 7+12+12 | 12+12+12 | 7+7+7+12 | 9+9+9+12
18 | 7+18 | 9+24 |  | 7+7+18 | 9+9+9 |  | 7+7+9+9 | 
24 | 7+24 | 12+12 |  | 7+9+9 | 9+9+12 |  | 7+7+9+12 | 
Maximum combination is 130%
PS : maximum combination is based on not all indoor units will turn on at the same time.
Basic Information Features

## Slide 15
Product line Basic Information
Installation combination
One unit | Two unit |  | Three unit |  |  |  | Four unit |  |  | 
7 | 7+7 | 9+18 | 7+7+7 | 7+9+18 | 9+9+12 | 12+12+12 | 7+7+7+7 | 7+7+9+18 | 7+9+12+12 | 9+12+12+12
9 | 7+9 | 9+24 | 7+7+9 | 7+9+24 | 9+9+18 | 12+12+18 | 7+7+7+9 | 7+7+9+24 | 7+9+12+18 | 
12 | 7+12 | 12+12 | 7+7+12 | 7+12+12 | 9+9+24 |  | 7+7+7+12 | 7+7+12+12 | 7+12+12+12 | 
18 | 7+18 | 12+18 | 7+7+18 | 7+12+18 | 9+12+12 |  | 7+7+7+18 | 7+7+12+18 | 9+9+9+9 | 
24 | 7+24 | 12+24 | 7+7+24 | 7+12+24 | 9+12+18 |  | 7+7+7+24 | 7+9+9+9 | 9+9+9+12 | 
 | 9+9 | 18+18 | 7+9+9 | 7+18+18 | 9+12+24 |  | 7+7+9+9 | 7+9+9+12 | 9+9+9+18 | 
 | 9+12 |  | 7+9+12 | 9+9+9 | 9+18+18 |  | 7+7+9+12 | 7+9+9+18 | 9+9+12+12 | 
Combination table for 36K
Maximum combination is 130%
PS : maximum combination is based on not all indoor units will turn on at the same time.
Basic Information Features

## Slide 16
Product line Basic Information
Installation combination
Combination table for 42K
One Unit | Two Unit | Three Unit |  | Four Unit |  |  | Five Unit |  | 
7 | 7+7 | 7+7+7 | 9+9+9 | 7+7+7+7 | 7+9+9+9 | 9+9+9+24 | 7+7+7+7+7 | 7+7+9+9+18 | 9+9+9+12+12
9 | 7+9 | 7+7+9 | 9+9+12 | 7+7+7+9 | 7+9+9+12 | 9+9+12+12 | 7+7+7+7+9 | 7+7+9+12+12 | 9+9+12+12+12
12 | 7+12 | 7+7+12 | 9+9+18 | 7+7+7+12 | 7+9+9+18 | 9+9+12+18 | 7+7+7+7+12 | 7+7+9+12+18 | 
18 | 7+18 | 7+7+18 | 9+9+24 | 7+7+7+18 | 7+9+9+24 | 9+9+12+24 | 7+7+7+7+18 | 7+7+12+12+12 | 
24 | 7+24 | 7+7+24 | 9+12+12 | 7+7+7+24 | 7+9+12+12 | 9+12+12+12 | 7+7+7+7+24 | 7+7+12+12+18 | 
 | 9+9 | 7+9+9 | 9+12+18 | 7+7+9+9 | 7+9+12+18 | 9+12+12+18 | 7+7+7+9+9 | 7+9+9+9+9 | 
 | 9+12 | 7+9+12 | 9+12+24 | 7+7+9+12 | 7+9+12+24 | 12+12+12+12 | 7+7+7+9+12 | 7+9+9+9+12 | 
 | 9+18 | 7+9+18 | 9+18+18 | 7+7+9+18 | 7+9+18+18 | 12+12+12+18 | 7+7+7+9+18 | 7+9+9+9+18 | 
 | 9+24 | 7+9+24 | 12+12+12 | 7+7+9+24 | 7+12+12+12 |  | 7+7+7+9+24 | 7+9+9+12+12 | 
 | 12+12 | 7+12+12 | 12+12+18 | 7+7+12+12 | 7+12+12+18 |  | 7+7+7+12+12 | 7+9+12+12+12 | 
 | 12+18 | 7+12+18 | 12+12+24 | 7+7+12+18 | 9+9+9+9 |  | 7+7+7+12+18 | 9+9+9+9+9 | 
 | 12+24 | 7+12+24 | 12+18+18 | 7+7+12+24 | 9+9+9+12 |  | 7+7+9+9+9 | 9+9+9+9+12 | 
 | 18+18 | 7+18+18 |  | 7+7+18+18 | 9+9+9+18 |  | 7+7+9+9+12 | 9+9+9+9+18 | 
Maximum combination is 130%
PS : maximum combination is based on not all indoor units will turn on at the same time.
Basic Information Features

## Slide 17
Product line Basic Information
Working temperature range
Mode | Cooling | Heating
Room temp. | 17~32 | 0~30
Outside ambient temp. | -15~ 50 | -15~ 24
Basic Information Features

## Slide 18
Product line Basic Information
Basic information for key components
Compressor: DC Inverter Rotary type
Indoor fan motor: Max. 220-240V,
Outdoor fan motor: 220-240V, 50Hz
Swing motor: DC12V
Four-way valve: 220-240V, 50Hz, energized in heating mode
Transformer: Input 220-240V, 50Hz, output 12-14V
Electronic expansive valve: DC 12V
Basic Information Features

## Slide 19
Part II Features

## Slide 20
Basic Information Features
Auto-correction Easy Maintenance Compatible Reliable
Notes: Compare to mono system, some functions of multi system are un available, such as Clean, Refrigerant detection, Silent,
1W standby,ECO, Breeze away ,Emergency Using,Gear.
● | Standard
◎ | Could optional
X | No this function
Notes: This features list base on
EU product
and specific remote controller,
it is only for reference.

## Slide 21
Basic Information Features
Auto-correction Easy Maintenance Compatible Reliable
Notes: Compare to mono system, some functions of multi system are un available, such as Clean, Refrigerant detection, Silent,
1W standby,ECO, Emergency Using, Breeze away, Gear.
● | Standard
◎ | Could optional
X | No this function
Notes: This features list base on EU product
and specific remote controller, it is only for reference.

## Slide 22
Automatic wiring/piping correction function (new feature)
Basic Information Features
Auto-correction Easy Maintenance Compatible Reliable
New product is capable of automatic correction of wiring/piping error.
Press the "check switch" on the outdoor unit PCB board 5 seconds until LED display "CE", which mean this function is working, Approximately 5-10 minutes after the switch is pressed, the "CE" disappear the wiring/piping error will be corrected, and wiring/piping is properly connected.
Incorrect wiring
Liquid/gas pipe
Terminal block
Outdoor unit
Indoor unit A
Indoor unit B
Before

## Slide 23
Automatic wiring/piping correction function (new feature)
Incorrect wiring
Liquid/gas pipe
Terminal block
Outdoor unit
Indoor unit A
Indoor unit B
Now
Conditions:
1. Check at outside temperature is above 5℃. (This function does not work when outside temperature is not above 5℃) 2. Check that the stop valves of the liquid pipe and gas pipe are open. 3. Turn on the breaker and wait at least 2 minute. 4. Press the check switch on the outdoor PCB board unit LED display "CE".
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 24
Automatic wiring/piping correction function (new feature)
New product is capable of automatic correction of wiring/piping error.
Press the "check switch" on the outdoor unit PCB board 5 seconds until LED display "CE", which mean this function is working, Approximately 5-10 minutes after the switch is pressed, the "CE" disappear the wiring/piping error will be corrected, and wiring/piping is properly connected.
Check switch
LED display
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 25
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Check point button
Status and Error Display
Press this button to check operation
parameters when the unit is running.
Display operation status and error codes.
Basic Information Features

## Slide 26
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features
Digital Display
Check Button
In standby, the LED displays “- -”.
In compressor operation, the LED displays the running frequency.
In defrosting mode, The LED displays “dF” or alternative displays between running frequency and “dF”(each displays 2s).
In protection or malfunction, the LED displays error code or protection code.
With the check button and digital display, many useful information will be showed.
Every time the button is pressed, the item code will be showed for 1.5 second, then the information will be showed.

## Slide 27
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features
No. | Display | Remark
00 | Normal display | Display running frequency, running state or malfunction code
01 | Number of indoor units in good connection | Actual data
02 | Outdoor unit running mode | 0-Standby, 1-Fan only, 2-Cooling, 3-Heating, 4-Forced cooling
03 | A indoor unit capacity HP | 7K: HP=0.8, 9K: HP=1.0, 12K: HP=1.2, 18K: HP=1.5 If the indoor unit is not connected, the digital display tube will show: “――”
04 | B indoor unit capacity HP | 
05 | C indoor unit capacity HP | 
06 | D indoor unit capacity HP | 
07 | E indoor unit capacity HP | 
08 | A Indoor unit capacity demand code | Norm value*HP
09 | B Indoor unit capacity demand code | 
10 | C Indoor unit capacity demand code | 
11 | D Indoor unit capacity demand code | 
12 | E Indoor unit capacity demand code | 
13 | Total indoor units amendatory capacity demand code | 7 for Forced cooling mode
14 | Target frequency corresponding to the total indoor units amendatory capacity demand | 
Push the button, you can check some parameters on display tube when the unit is running.

## Slide 28
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features
No. | Display | Remark
15 | Target frequency after the frequency limit | 
16 | Target frequency sending to compressor control chip | 
17 | A indoor unit evaporator outlet temp.(T2BA) | If the temp. is lower than -9 degree, the digital display tube will show “-9”.If the temp. is higher than 70 degree, the digital display tube will show “70”. If the indoor unit is not connected, the digital display tube will show: “――”
18 | B indoor unit evaporator outlet temp.(T2BB) | 
19 | C indoor unit evaporator outlet temp.(T2BC) | 
20 | D indoor unit evaporator outlet temp.(T2BD) | 
21 | E indoor unit evaporator outlet temp.(T2BE) | 
22 | A indoor unit room temp.(T1A) | If the temp. is lower than 0 degree, the digital display tube will show “0”.If the temp. is higher than 50 degree, the digital display tube will show “50”. If the indoor unit is not connected, the digital display tube will show: “――”
23 | B indoor unit room temp.(T1B) | 
24 | C indoor unit room temp.(T1C) | 
25 | D indoor unit room temp.(T1D) | 
26 | E indoor unit room temp.(T1E) | 
27 | A indoor unit evaporator temp.(T2A) | If the temp. is lower than -9 degree, the digital display tube will show “-9”.If the temp. is higher than 70 degree, the digital display tube will show “70”. If the indoor unit is not connected, the digital display tube will show: “――”
28 | B indoor unit evaporator temp.(T2B) | 
29 | C indoor unit evaporator temp.(T2C) | 
30 | D indoor unit evaporator temp.(T2D) | 
31 | E indoor unit evaporator temp.(T2E) | 

## Slide 29
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features
No. | Display | Remark
32 | Condenser pipe temp.(T3) | If the temp. is lower than -9 degree, the digital display tube will show “-9”.If the temp. is higher than 70 degree, the digital display tube will show “70”.
33 | Outdoor ambient temp.(T4) | 
34 | Compressor discharge temp.(Tp) | The display value is between 30~129 degree. If the temp. is lower than 30 degree, the digital display tube will show “30”.If the temp. is higher than 99 degree, the digital display tube will show single digit and tens digit. For example, the digital display tube show “0.5”,it means the compressor discharge temp. is 105 degree.)
35 | AD value of current | The display value is hex number. For example ,the digital display tube show “Cd”, it means AD value is 205.
36 | AD value of voltage | 
37 | EEV open angle for A indoor unit | Actual data/4. If the value is higher than 99, the digital display tube will show single digit and tens digit. For example ,the digital display tube show “2.0”,it means the EEV open angle is 120×4=480p.)
38 | EEV open angle for B indoor unit | 
39 | EEV open angle for C indoor unit | 
40 | EEV open angle for D indoor unit | 
41 | EEV open angle for E indoor unit | 

## Slide 30
Outdoor check function
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features
No. | Display | Remark |  | 
42 | Frequency limit symbol | Bit7 | Frequency limit caused by IGBT radiator | The display value is hex number. For example, the digital display tube show 2A,then Bit5=1, Bit3=1, Bit1=1. It means frequency limit caused by T4,T3 and current.
 |  | Bit6 | Frequency limit caused by PFC | 
 |  | Bit5 | Frequency limit caused by T4. | 
 |  | Bit4 | Frequency limit caused by T2. | 
 |  | Bit3 | Frequency limit caused by T3. | 
 |  | Bit2 | Frequency limit caused by Tp. | 
 |  | Bit1 | Frequency limit caused by current | 
 |  | Bit0 | Frequency limit caused by voltage | 
43 | Average value of T2 | (Sum T2 value of all indoor units)/(indoor units number) |  | 
44 | Outdoor fan speed | 0- Off, 1- High speed, 2- Med speed, 3- Low speed, 4- breeze speed, 5- Super breeze speed |  | 
45 | The last error or protection code | 00 means no error or protection |  | 

## Slide 31
Compatible indoor unit for both mono and multi inverter system.
The advantage for us: It comes in handy for warehouse and stock administration.
Models | Split | Cassette | Duct | Console
7K | Y | N | N | N
9K | Y | N | N | N
12K | Y | Y | Y | Y
18K | Y | Y | Y | Y
24K | Y | Y | Y | Y
Mono & Multi Compatible (standard)
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 32
Mono & Multi Compatible (standard)
Auto-correction Easy Maintenance Compatible Reliable
Power Supply
Outdoor Unit
Indoor Unit
Ralay
Wiring of mono system
Wiring of multi system
Power Supply
Outdoor Unit
Indoor Unit
Not connected
A relay(RY) is placed between the W and 1(L) of the indoor PCB. It can cut off the power of outdoor unit when the unit is in standby mode, helping realize 1W standby function.
W,1(L) : Live line
2(N) : Zero line
S : Signal line
Basic Information Features

## Slide 33
Setting mode | Cooling | Heating | Fan | Off
Cooling | No | Yes | No | No
Heating | Yes | No | Yes | No
Fan | No | Yes | No | No
Off | No | No | No | No
Note: ”Yes” means mode conflict, “No” means no mode conflict.
Mode conflict
When there are different mode settings among active indoor units, system will define as following:
Heating mode will have a priority.
Cooling mode and Fan mode will conflict to heating mode.
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 34
Mode conflict
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 35
Mode conflict
Auto-correction Easy Maintenance Compatible Reliable
Basic Information Features

## Slide 36
Part III Difference Multi
between old and new

## Slide 37
Difference1
ODU chassis changed
(1 drive 2) 14K, 18K X3(805x330x554mm)
(1 drive 2) 14K, 18K B(800x333x554mm)
Old
New

## Slide 38
Difference1
ODU chassis changed
Old
New
(1 drive 3) 21K, 27K
X4(890x342x673mm)
(1 drive 3) 21K, 27K
CA(845x363x702mm)

## Slide 39
Difference2
Wiring diagram
Old Carrier Model | Wiring diagram | New Carrier Model | Wiring diagram | Notes
38QUS014D8S2 | 16022300002793 | 38QUS014D8S2-1 | 16022300002793 | remain
38QUS018D8S2-1 | 16022300002793 | 38QUS018D8S2-2 | 16022000031469 | change
38QUS021D8S3 | 16022000035910 | 38QUS021D8S3-1 | 16022300000797 | change
38QUS027D8S3-1 | 16022000035910 | 38QUS027D8S3-2 | 16022300000797 | change
Notes: as the whole ODU chassis updated，the wiring diagram changed, pls refer to service manual details

## Slide 40
Difference 3
Key components change
Notes: as the whole ODU chassis updated，the wiring diagram changed, pls refer to service manual details
14K |  |  | 18K |  | 
Key component | Old | New | Key component | Old | New
compressor model | KSN140D21UFZ | KSN140D58UFZ | compressor model | KSN140D21UFZ | KSN140D58UFZ
Fan motor model | ZKFN-34-8-1-3 | ZKFN-34-10-1 | Fan motor model | ZKFN-34-8-1-3 | ZKFN-34-10-1
Coil | 870x504x22 | keep the same | Coil | 860x508x44 | keep the same
21K |  |  | 27K |  | 
Key component | Old | New | Key component | Old | New
compressor model | KSN140D21UFZ | KSN140D58UFZ | compressor model | KTM240D57UMT | keep the same
Fan motor model | ZKFN-50-8-2-3 | ZKFN-80-8-3 | Fan motor model | ZKFN-50-8-2-3 | ZKFN-80-8-3
Coil | 730x651x44 | 900x609x22+ 540x609x22 | Coil | 735x*660x44 | 900x609x22+ 865x609x22

## Slide 41
Other Differences
Notes: as the ODU change, the performance also change, pls refer to spec details .