## Hi-wall
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
WALL-MOUNTED
Indoor unit(s) | : | 42QHF009DS x 3
Outdoor unit | : | 38QUS027DS3
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 7.9 | kW | cooling | SEER | 5.82 | -
heating/Average | Pdesignh | 8.202 | kW | heating/Average | SCOP/A | 3.82 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 8.4 | kW | Tj = 35℃ | EERd | 3.07 | -
Tj = 30℃ | Pdc | 6.225 | kW | Tj = 30℃ | EERd | 4.81 | -
Tj = 25℃ | Pdc | 4.188 | kW | Tj = 25℃ | EERd | 7.78 | -
Tj = 20℃ | Pdc | 2.616 | kW | Tj = 20℃ | EERd | 11.89 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 7.431 | kW | Tj = -7℃ | COPd | 2.52 | -
Tj = 2℃ | Pdh | 4.63 | kW | Tj = 2℃ | COPd | 3.63 | -
Tj = 7℃ | Pdh | 3.1 | kW | Tj = 7℃ | COPd | 5.26 | -
Tj = 12℃ | Pdh | 3.022 | kW | Tj = 12℃ | COPd | 6.09 | -
Tj = bivalent temperature | Pdh | 7.431 | kW | Tj = bivalent temperature | COPd | 2.52 | -
Tj = operating limit | Pdh | 6.086 | kW | Tj = operating limit | COPd | 2.11 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.016 | kW | cooling | QCE | 477 | kWh/a
standby mode | Psb | 0.016 | kW | heating/Average | Qhe | 3021 | kWh/a
thermostat-off mode | Pto | 0.074 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 55/67 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Ducted
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Ducted
Indoor unit(s) | : | 42QSM009DS x 3
Outdoor unit | : | 38QUS027DS3
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 7.9 | kW | cooling | SEER | 5.82 | -
heating/Average | Pdesignh | 8.202 | kW | heating/Average | SCOP/A | 3.82 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 7.9 | kW | Tj = 35℃ | EERd | 2.98 | -
Tj = 30℃ | Pdc | 5.809 | kW | Tj = 30℃ | EERd | 4.54 | -
Tj = 25℃ | Pdc | 3.685 | kW | Tj = 25℃ | EERd | 7.09 | -
Tj = 20℃ | Pdc | 2.485 | kW | Tj = 20℃ | EERd | 11.19 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 7.256 | kW | Tj = -7℃ | COPd | 2.68 | -
Tj = 2℃ | Pdh | 4.465 | kW | Tj = 2℃ | COPd | 3.63 | -
Tj = 7℃ | Pdh | 3.056 | kW | Tj = 7℃ | COPd | 5.03 | -
Tj = 12℃ | Pdh | 3.098 | kW | Tj = 12℃ | COPd | 6.12 | -
Tj = bivalent temperature | Pdh | 7.256 | kW | Tj = bivalent temperature | COPd | 2.45 | -
Tj = operating limit | Pdh | 7.219 | kW | Tj = operating limit | COPd | 2.68 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.0113 | kW | cooling | QCE | 477 | kWh/a
standby mode | Psb | 0.0113 | kW | heating/Average | Qhe | 3021 | kWh/a
thermostat-off mode | Pto | 0.0395 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 55/67 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Cassette
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Cassette
Indoor unit(s) | : | 42QTD009DS x 3
Outdoor unit | : | 38QUS027DS3
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 7.9 | kW | cooling | SEER | 5.82 | -
heating/Average | Pdesignh | 8.202 | kW | heating/Average | SCOP/A | 3.82 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 7.9 | kW | Tj = 35℃ | EERd | 2.98 | -
Tj = 30℃ | Pdc | 5.809 | kW | Tj = 30℃ | EERd | 4.54 | -
Tj = 25℃ | Pdc | 3.685 | kW | Tj = 25℃ | EERd | 7.09 | -
Tj = 20℃ | Pdc | 2.485 | kW | Tj = 20℃ | EERd | 11.19 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 7.256 | kW | Tj = -7℃ | COPd | 2.68 | -
Tj = 2℃ | Pdh | 4.465 | kW | Tj = 2℃ | COPd | 3.63 | -
Tj = 7℃ | Pdh | 3.056 | kW | Tj = 7℃ | COPd | 5.03 | -
Tj = 12℃ | Pdh | 3.098 | kW | Tj = 12℃ | COPd | 6.12 | -
Tj = bivalent temperature | Pdh | 7.256 | kW | Tj = bivalent temperature | COPd | 2.45 | -
Tj = operating limit | Pdh | 7.219 | kW | Tj = operating limit | COPd | 2.68 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.0113 | kW | cooling | QCE | 477 | kWh/a
standby mode | Psb | 0.0113 | kW | heating/Average | Qhe | 3021 | kWh/a
thermostat-off mode | Pto | 0.0395 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 54/67 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.

## Console
Information requirements
This information includes the results of calculation of the seasonal energy consumption and efficiency for air conditioner in regards to ErP pursuant to the Commission Regulation(EU) No.206/2012 and No.626/2011. Information to identify the model(s) to which the information relates to:
TYPE | : | AIR CONDITIONER
MULTI SPLIT
Console
Indoor unit(s) | : | 42QFA009DS x 3
Outdoor unit | : | 38QUS027DS3
Brand | : | Carrier
Function (indicate if present) |  |  |  | if fuction includes heating : Indicate the heating season the information relates to. Indicated values should relate to one heating season at a time. Include at least the heating season 'Average'.
cooling |  | Y |  | Average (mandatory) |  | Y
heating |  | Y |  | Warmer (if designated) |  | N
|  |  |  | Colder (if designated) |  | N
Item | symbol | value | unit | Item | symbol | value | unit
Design load |  |  |  | Seasonal efficiency
cooling | Pdesignc | 7.9 | kW | cooling | SEER | 5.82 | -
heating/Average | Pdesignh | 8.202 | kW | heating/Average | SCOP/A | 3.82 | -
heating/Warmer | Pdesignh | x,x | kW | heating/Warmer | SCOP/W | x,x | -
heating/Colder | Pdesignh | x,x | kW | heating/Colder | SCOP/C | x,x | -
Declared capacity(*) for cooling, at indoor temperature 27(19)℃ and outdoor temperature Tj |  |  |  | Declared energy efficiency ratio(*), at indoor temperature 27(19)℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 35℃ | Pdc | 7.9 | kW | Tj = 35℃ | EERd | 2.4891 | -
Tj = 30℃ | Pdc | 5.457 | kW | Tj = 30℃ | EERd | 4.307 | -
Tj = 25℃ | Pdc | 3.523 | kW | Tj = 25℃ | EERd | 7.7599 | -
Tj = 20℃ | Pdc | 1.945 | kW | Tj = 20℃ | EERd | 13.6014 | -
Declared capacity(*) for heating/Average season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Average season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | 7.431 | kW | Tj = -7℃ | COPd | 2.5695 | -
Tj = 2℃ | Pdh | 4.459 | kW | Tj = 2℃ | COPd | 3.5844 | -
Tj = 7℃ | Pdh | 3.005 | kW | Tj = 7℃ | COPd | 5.3565 | -
Tj = 12℃ | Pdh | 3.124 | kW | Tj = 12℃ | COPd | 6.6468 | -
Tj = bivalent temperature | Pdh | 7.431 | kW | Tj = bivalent temperature | COPd | 2.57 | -
Tj = operating limit | Pdh | 6.215 | kW | Tj = operating limit | COPd | 2.14 | -
Declared capacity(*) for heating/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Warmer season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Declared capacity(*) for heating/Colder season, at indoor temperature 20℃ and outdoor temperature Tj |  |  |  | Declared coefficient of performance(*)/Colder season, at indoor temperature 20℃ and outdoor temperature Tj
Item | symbol | value | unit | Item | symbol | value | unit
Tj = -7℃ | Pdh | x,x | kW | Tj = -7℃ | COPd | x,x | -
Tj = 2℃ | Pdh | x,x | kW | Tj = 2℃ | COPd | x,x | -
Tj = 7℃ | Pdh | x,x | kW | Tj = 7℃ | COPd | x,x | -
Tj = 12℃ | Pdh | x,x | kW | Tj = 12℃ | COPd | x,x | -
Tj = bivalent temperature | Pdh | x,x | kW | Tj = bivalent temperature | COPd | x,x | -
Tj = operating limit | Pdh | x,x | kW | Tj = operating limit | COPd | x,x | -
Tj = -15℃ | Pdh | x,x | kW | Tj = -15℃ | COPd | x,x | -
Bivalent temperature |  |  |  | Operating limit temperature
heating/Average | Tbiv | -7 | ℃ | heating/Average | Tol | -15 | ℃
heating/Warmer | Tbiv | x | ℃ | heating/Warmer | Tol | x | ℃
heating/Colder | Tbiv | x | ℃ | heating/Colder | Tol | x | ℃
Cycling interval capacity |  |  |  | Cycling interval efficiency
for cooling | Pcycc | x,x | kW | heating/Average | EERcyc | x,x | -
for heating | Pcych | x,x | kW | heating/Warmer | COPcyc | x,x | -
Degradation co-efficient cooling | Cdc | 0.25 | - | Degradation co-efficient heating | Cdc | 0.25 | -
Electric power input in power modes other than 'active mode' |  |  |  | Annual electricity consumption
off mode | Poff | 0.0105 | kW | cooling | QCE | 477 | kWh/a
standby mode | Psb | 0.0105 | kW | heating/Average | Qhe | 3021 | kWh/a
thermostat-off mode | Pto | 0.0146 | kW | heating/Warmer | Qhe | x | kWh/a
crankcase heater mode | Pck | 0 | kW | heating/Colder | Qhe | x | kWh/a
Capacity control(indicate one of the options) |  |  |  | Other items
Item | symbol | value | unit | Item | symbol | value | unit
fixed | N |  |  | Sound power level (indoor/outdoor) | LWA | 57/67 | dB(A)
staged | N |  |  | Global warning potential | GWP | 2088 | kgCO2 eq
variable | Y |  |  | Rated air flow (indoor/outdoor) | - | x/x | m3/h
Contact details for obtaining more information | Company: Foshan Midea Carrier Air-Conditioning Equipment Co. Ltd Address: Northern of No.5 Industrial District of Midea, ShunDe, Foshan City, Guangdong Province, P.R. China 528311 Telephone: +86-757-26338546 Fax: +86-757-26337977
Note on G50: 匿名用户: We will test at -15.