# Capacity Tables For New Ducted R32 Series

**Cooling**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS012D8S-1+38QUS012D8S-1 | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 300 | -15 | TC | 3.71 | 3.72 | 3.72 | 3.72 | 3.90 | 3.96 | 3.96 | 3.96 | 4.00 | 4.00 | 4.00 | 4.00 | 4.25 | 4.25 | 4.25 | 4.25 |
| S/T | 0.65 | 0.70 | 0.76 | 0.81 | 0.55 | 0.60 | 0.66 | 0.70 | 0.50 | 0.55 | 0.60 | 0.66 | 0.39 | 0.43 | 0.48 | 0.53 |
| PI | 0.70 | 0.70 | 0.70 | 0.70 | 0.69 | 0.69 | 0.69 | 0.69 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 |
| -10 | TC | 3.68 | 3.70 | 3.70 | 3.70 | 3.87 | 3.93 | 3.93 | 3.93 | 3.98 | 3.98 | 3.98 | 3.98 | 4.23 | 4.23 | 4.23 | 4.23 |
| S/T | 0.65 | 0.71 | 0.77 | 0.82 | 0.55 | 0.61 | 0.66 | 0.71 | 0.50 | 0.55 | 0.60 | 0.66 | 0.39 | 0.44 | 0.49 | 0.53 |
| PI | 0.70 | 0.70 | 0.70 | 0.70 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.70 | 0.70 | 0.70 | 0.70 |
| -5 | TC | 3.66 | 3.67 | 3.67 | 3.67 | 3.86 | 3.92 | 3.92 | 3.92 | 3.96 | 3.96 | 3.96 | 3.96 | 4.22 | 4.22 | 4.22 | 4.22 |
| S/T | 0.65 | 0.71 | 0.77 | 0.82 | 0.56 | 0.61 | 0.66 | 0.71 | 0.51 | 0.56 | 0.60 | 0.66 | 0.39 | 0.44 | 0.49 | 0.54 |
| PI | 0.69 | 0.70 | 0.70 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.70 | 0.70 | 0.70 | 0.70 |
| 0 | TC | 3.64 | 3.66 | 3.66 | 3.66 | 3.85 | 3.91 | 3.91 | 3.91 | 3.95 | 3.95 | 3.95 | 3.95 | 4.22 | 4.22 | 4.22 | 4.22 |
| S/T | 0.66 | 0.72 | 0.77 | 0.82 | 0.56 | 0.61 | 0.67 | 0.72 | 0.51 | 0.56 | 0.61 | 0.67 | 0.39 | 0.44 | 0.49 | 0.54 |
| PI | 0.70 | 0.70 | 0.70 | 0.70 | 0.69 | 0.69 | 0.69 | 0.69 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 |
| 5 | TC | 3.62 | 3.64 | 3.64 | 3.64 | 3.83 | 3.89 | 3.89 | 3.89 | 3.94 | 3.94 | 3.94 | 3.94 | 4.21 | 4.21 | 4.21 | 4.21 |
| S/T | 0.66 | 0.72 | 0.78 | 0.83 | 0.56 | 0.61 | 0.67 | 0.72 | 0.51 | 0.56 | 0.61 | 0.67 | 0.39 | 0.44 | 0.49 | 0.54 |
| PI | 0.70 | 0.71 | 0.71 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.71 | 0.71 | 0.71 | 0.71 |
| 10 | TC | 3.60 | 3.61 | 3.61 | 3.61 | 3.81 | 3.87 | 3.87 | 3.87 | 3.92 | 3.92 | 3.92 | 3.92 | 4.20 | 4.20 | 4.20 | 4.20 |
| S/T | 0.66 | 0.72 | 0.78 | 0.83 | 0.56 | 0.62 | 0.67 | 0.72 | 0.51 | 0.56 | 0.61 | 0.67 | 0.40 | 0.45 | 0.50 | 0.54 |
| PI | 0.72 | 0.72 | 0.72 | 0.72 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.72 | 0.72 | 0.72 | 0.72 |
| 15 | TC | 3.57 | 3.59 | 3.59 | 3.59 | 3.79 | 3.85 | 3.85 | 3.85 | 3.90 | 3.90 | 3.90 | 3.90 | 4.19 | 4.19 | 4.19 | 4.19 |
| S/T | 0.67 | 0.73 | 0.79 | 0.84 | 0.57 | 0.62 | 0.68 | 0.73 | 0.52 | 0.57 | 0.62 | 0.68 | 0.40 | 0.45 | 0.50 | 0.55 |
| PI | 0.73 | 0.74 | 0.74 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 |
| 20 | TC | 3.53 | 3.54 | 3.54 | 3.54 | 3.75 | 3.75 | 3.75 | 3.75 | 3.86 | 3.86 | 3.86 | 3.86 | 4.15 | 4.15 | 4.15 | 4.15 |
| S/T | 0.67 | 0.73 | 0.79 | 0.84 | 0.57 | 0.62 | 0.68 | 0.73 | 0.52 | 0.57 | 0.62 | 0.68 | 0.40 | 0.45 | 0.50 | 0.55 |
| PI | 0.76 | 0.76 | 0.76 | 0.76 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 |
| 25 | TC | 3.37 | 3.37 | 3.37 | 3.37 | 3.57 | 3.57 | 3.57 | 3.57 | 3.69 | 3.69 | 3.69 | 3.69 | 3.98 | 3.98 | 3.98 | 3.98 |
| S/T | 0.68 | 0.74 | 0.80 | 0.86 | 0.57 | 0.63 | 0.68 | 0.74 | 0.52 | 0.57 | 0.63 | 0.68 | 0.40 | 0.45 | 0.50 | 0.55 |
| PI | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 |
| 30 | TC | 3.20 | 3.20 | 3.20 | 3.20 | 3.43 | 3.43 | 3.43 | 3.43 | 3.52 | 3.52 | 3.52 | 3.52 | 3.80 | 3.80 | 3.80 | 3.80 |
| S/T | 0.68 | 0.74 | 0.81 | 0.87 | 0.57 | 0.63 | 0.69 | 0.74 | 0.52 | 0.57 | 0.63 | 0.69 | 0.39 | 0.45 | 0.50 | 0.55 |
| PI | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 |
| 35 | TC | 3.05 | 3.05 | 3.05 | 3.05 | 3.26 | 3.26 | 3.26 | 3.26 | 3.34 | 3.34 | 3.40 | 3.34 | 3.60 | 3.60 | 3.60 | 3.60 |
| S/T | 0.68 | 0.75 | 0.82 | 0.88 | 0.57 | 0.63 | 0.69 | 0.75 | 0.51 | 0.57 | 0.63 | 0.69 | 0.39 | 0.44 | 0.50 | 0.56 |
| PI | 1.00 | 1.00 | 1.00 | 1.00 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 1.02 |
| 40 | TC | 2.89 | 2.89 | 2.89 | 2.91 | 3.09 | 3.09 | 3.09 | 3.09 | 3.18 | 3.18 | 3.21 | 3.18 | 3.43 | 3.43 | 3.43 | 3.43 |
| S/T | 0.69 | 0.77 | 0.84 | 0.91 | 0.57 | 0.64 | 0.71 | 0.77 | 0.51 | 0.58 | 0.64 | 0.71 | 0.38 | 0.44 | 0.50 | 0.56 |
| PI | 1.10 | 1.10 | 1.10 | 1.10 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.12 | 1.12 | 1.12 | 1.12 |
| 46 | TC | 2.67 | 2.67 | 2.67 | 2.70 | 2.87 | 2.87 | 2.87 | 2.87 | 2.96 | 2.96 | 2.96 | 2.96 | 3.19 | 3.19 | 3.19 | 3.19 |
| S/T | 0.70 | 0.78 | 0.85 | 0.92 | 0.57 | 0.64 | 0.71 | 0.78 | 0.51 | 0.58 | 0.65 | 0.72 | 0.38 | 0.44 | 0.50 | 0.57 |
| PI | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.24 | 1.24 | 1.24 | 1.24 |
| 50 | TC | 2.53 | 2.53 | 2.53 | 2.55 | 2.70 | 2.70 | 2.70 | 2.70 | 2.79 | 2.79 | 2.79 | 2.79 | 3.02 | 3.02 | 3.02 | 3.02 |
| S/T | 0.71 | 0.79 | 0.87 | 0.95 | 0.57 | 0.65 | 0.72 | 0.80 | 0.51 | 0.59 | 0.66 | 0.73 | 0.37 | 0.44 | 0.50 | 0.57 |
| PI | 1.33 | 1.33 | 1.33 | 1.33 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.35 | 1.35 | 1.35 | 1.35 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 480 | -15 | TC | 3.78 | 3.78 | 3.81 | 3.84 | 3.96 | 3.96 | 3.96 | 3.96 | 4.06 | 4.06 | 4.06 | 4.06 | 4.31 | 4.31 | 4.31 | 4.31 |
| S/T | 0.70 | 0.79 | 0.98 | 1.00 | 0.56 | 0.65 | 0.72 | 0.81 | 0.50 | 0.58 | 0.66 | 0.73 | 0.35 | 0.42 | 0.49 | 0.57 |
| PI | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.71 | 0.71 | 0.71 | 0.71 |
| -10 | TC | 3.76 | 3.76 | 3.79 | 3.82 | 3.93 | 3.93 | 3.93 | 3.93 | 4.04 | 4.04 | 4.04 | 4.04 | 4.29 | 4.29 | 4.29 | 4.29 |
| S/T | 0.71 | 0.80 | 0.99 | 1.00 | 0.56 | 0.65 | 0.73 | 0.82 | 0.50 | 0.58 | 0.66 | 0.74 | 0.35 | 0.43 | 0.49 | 0.57 |
| PI | 0.71 | 0.71 | 0.71 | 0.71 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.71 | 0.71 | 0.71 | 0.71 |
| -5 | TC | 3.73 | 3.73 | 3.76 | 3.79 | 3.92 | 3.92 | 3.92 | 3.92 | 4.02 | 4.02 | 4.02 | 4.02 | 4.28 | 4.28 | 4.28 | 4.28 |
| S/T | 0.71 | 0.80 | 0.99 | 1.00 | 0.57 | 0.65 | 0.73 | 0.82 | 0.51 | 0.59 | 0.66 | 0.74 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.72 | 0.72 | 0.72 | 0.72 | 0.71 | 0.71 | 0.71 | 0.71 |
| 0 | TC | 3.72 | 3.72 | 3.75 | 3.77 | 3.91 | 3.91 | 3.91 | 3.91 | 4.01 | 4.01 | 4.01 | 4.01 | 4.28 | 4.28 | 4.28 | 4.28 |
| S/T | 0.72 | 0.80 | 1.00 | 1.00 | 0.57 | 0.66 | 0.74 | 0.82 | 0.51 | 0.59 | 0.67 | 0.74 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 0.71 | 0.71 | 0.71 | 0.71 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |
| 5 | TC | 3.70 | 3.70 | 3.73 | 3.76 | 3.89 | 3.89 | 3.89 | 3.89 | 4.00 | 4.00 | 4.00 | 4.00 | 4.27 | 4.27 | 4.27 | 4.27 |
| S/T | 0.72 | 0.81 | 1.00 | 1.00 | 0.57 | 0.66 | 0.74 | 0.83 | 0.51 | 0.59 | 0.67 | 0.75 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.73 | 0.72 | 0.72 | 0.72 | 0.72 |
| 10 | TC | 3.67 | 3.67 | 3.70 | 3.73 | 3.87 | 3.87 | 3.87 | 3.87 | 3.98 | 3.98 | 3.98 | 3.98 | 4.26 | 4.26 | 4.26 | 4.26 |
| S/T | 0.72 | 0.81 | 1.00 | 1.00 | 0.57 | 0.66 | 0.74 | 0.83 | 0.51 | 0.59 | 0.67 | 0.75 | 0.36 | 0.44 | 0.50 | 0.58 |
| PI | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.74 | 0.74 | 0.74 | 0.74 | 0.73 | 0.73 | 0.73 | 0.73 |
| 15 | TC | 3.64 | 3.64 | 3.67 | 3.70 | 3.85 | 3.85 | 3.85 | 3.85 | 3.96 | 3.96 | 3.96 | 3.96 | 4.25 | 4.25 | 4.25 | 4.25 |
| S/T | 0.73 | 0.82 | 0.90 | 0.99 | 0.58 | 0.67 | 0.75 | 0.84 | 0.52 | 0.60 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 |
| 20 | TC | 3.60 | 3.60 | 3.63 | 3.66 | 3.81 | 3.81 | 3.81 | 3.81 | 3.92 | 3.92 | 3.92 | 3.92 | 4.21 | 4.21 | 4.21 | 4.21 |
| S/T | 0.73 | 0.82 | 0.90 | 0.99 | 0.58 | 0.67 | 0.75 | 0.84 | 0.52 | 0.60 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.77 | 0.77 | 0.77 | 0.77 |
| 25 | TC | 3.43 | 3.43 | 3.46 | 3.49 | 3.63 | 3.63 | 3.63 | 3.63 | 3.75 | 3.75 | 3.75 | 3.75 | 4.04 | 4.04 | 4.04 | 4.04 |
| S/T | 0.74 | 0.83 | 0.92 | 1.00 | 0.59 | 0.68 | 0.77 | 0.85 | 0.52 | 0.60 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 |
| 30 | TC | 3.26 | 3.26 | 3.29 | 3.32 | 3.49 | 3.49 | 3.49 | 3.49 | 3.57 | 3.57 | 3.57 | 3.57 | 3.86 | 3.86 | 3.86 | 3.86 |
| S/T | 0.75 | 0.85 | 0.94 | 1.00 | 0.59 | 0.68 | 0.78 | 0.87 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.60 |
| PI | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 |
| 35 | TC | 3.11 | 3.11 | 3.14 | 3.17 | 3.32 | 3.32 | 3.32 | 3.34 | 3.40 | 3.40 | 3.46 | 3.40 | 3.66 | 3.66 | 3.66 | 3.66 |
| S/T | 0.76 | 0.86 | 0.96 | 1.00 | 0.60 | 0.69 | 0.79 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.61 |
| PI | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 |
| 40 | TC | 2.89 | 2.91 | 2.94 | 2.96 | 3.08 | 3.08 | 3.08 | 3.11 | 3.17 | 3.17 | 3.20 | 3.17 | 3.42 | 3.42 | 3.42 | 3.42 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.93 | 0.53 | 0.63 | 0.74 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.15 | 1.15 | 1.15 | 1.15 |
| 46 | TC | 2.68 | 2.71 | 2.73 | 2.76 | 2.85 | 2.85 | 2.85 | 2.88 | 2.93 | 2.93 | 2.93 | 2.93 | 3.19 | 3.19 | 3.19 | 3.19 |
| S/T | 0.80 | 0.91 | 1.00 | 1.00 | 0.62 | 0.73 | 0.84 | 0.95 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.26 | 1.26 | 1.26 | 1.26 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.28 | 1.28 | 1.28 | 1.28 |
| 50 | TC | 2.51 | 2.53 | 2.56 | 2.59 | 2.68 | 2.68 | 2.68 | 2.71 | 2.76 | 2.76 | 2.76 | 2.79 | 3.02 | 3.02 | 3.02 | 3.02 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.91 |
| PI | 1.37 | 1.37 | 1.37 | 1.37 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.39 | 1.39 | 1.39 | 1.39 |
| 600 | -15 | TC | 3.84 | 3.87 | 3.90 | 3.93 | 4.02 | 4.02 | 4.02 | 4.05 | 4.12 | 4.12 | 4.12 | 4.12 | 4.40 | 4.40 | 4.40 | 4.40 |
| S/T | 0.74 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.98 | 0.51 | 0.61 | 0.70 | 0.80 | 0.34 | 0.42 | 0.51 | 0.61 |
| PI | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 |
| -10 | TC | 3.82 | 3.85 | 3.88 | 3.91 | 3.99 | 3.99 | 3.99 | 4.02 | 4.10 | 4.10 | 4.10 | 4.10 | 4.38 | 4.38 | 4.38 | 4.38 |
| S/T | 0.75 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.98 | 0.51 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.51 | 0.61 |
| PI | 0.73 | 0.73 | 0.73 | 0.73 | 0.72 | 0.72 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 |
| -5 | TC | 3.79 | 3.82 | 3.85 | 3.88 | 3.98 | 3.98 | 3.98 | 4.01 | 4.08 | 4.08 | 4.08 | 4.08 | 4.37 | 4.37 | 4.37 | 4.37 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.99 | 0.52 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.52 | 0.61 |
| PI | 0.73 | 0.73 | 0.73 | 0.73 | 0.72 | 0.72 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 |
| 0 | TC | 3.77 | 3.80 | 3.83 | 3.86 | 3.96 | 3.96 | 3.96 | 3.99 | 4.07 | 4.07 | 4.07 | 4.07 | 4.37 | 4.37 | 4.37 | 4.37 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.99 | 0.52 | 0.62 | 0.72 | 0.81 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 |
| 5 | TC | 3.76 | 3.79 | 3.82 | 3.84 | 3.95 | 3.95 | 3.95 | 3.98 | 4.06 | 4.06 | 4.06 | 4.06 | 4.36 | 4.36 | 4.36 | 4.36 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 0.74 | 0.74 | 0.74 | 0.74 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.74 | 0.74 | 0.74 | 0.74 |
| 10 | TC | 3.73 | 3.76 | 3.79 | 3.82 | 3.93 | 3.93 | 3.93 | 3.96 | 4.04 | 4.04 | 4.04 | 4.04 | 4.35 | 4.35 | 4.35 | 4.35 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.35 | 0.44 | 0.52 | 0.62 |
| PI | 0.75 | 0.75 | 0.75 | 0.75 | 0.74 | 0.74 | 0.74 | 0.74 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 |
| 15 | TC | 3.70 | 3.73 | 3.76 | 3.79 | 3.90 | 3.90 | 3.90 | 3.93 | 4.02 | 4.02 | 4.02 | 4.02 | 4.33 | 4.33 | 4.33 | 4.33 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 0.77 | 0.77 | 0.77 | 0.77 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 |
| 20 | TC | 3.66 | 3.69 | 3.72 | 3.75 | 3.86 | 3.86 | 3.86 | 3.89 | 3.98 | 3.98 | 3.98 | 3.98 | 4.30 | 4.30 | 4.30 | 4.30 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 0.80 | 0.80 | 0.80 | 0.80 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 |
| 25 | TC | 3.49 | 3.52 | 3.55 | 3.57 | 3.69 | 3.69 | 3.69 | 3.72 | 3.81 | 3.81 | 3.81 | 3.81 | 4.09 | 4.09 | 4.09 | 4.09 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.94 | 0.53 | 0.64 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 |
| 30 | TC | 3.32 | 3.34 | 3.37 | 3.40 | 3.55 | 3.55 | 3.55 | 3.57 | 3.63 | 3.63 | 3.63 | 3.63 | 3.92 | 3.92 | 3.92 | 3.92 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.96 | 0.96 | 0.96 | 0.96 |
| 35 | TC | 3.14 | 3.17 | 3.20 | 3.23 | 3.37 | 3.37 | 3.37 | 3.40 | 3.46 | 3.46 | 3.52 | 3.55 | 3.75 | 3.75 | 3.75 | 3.75 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.98 | 0.54 | 0.66 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 1.04 | 1.04 | 1.04 | 1.04 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.06 | 1.06 | 1.06 | 1.06 |
| 40 | TC | 2.92 | 2.95 | 2.98 | 3.01 | 3.14 | 3.14 | 3.15 | 3.18 | 3.22 | 3.22 | 3.25 | 3.28 | 3.50 | 3.50 | 3.50 | 3.50 |
| S/T | 0.85 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.80 | 0.93 | 0.33 | 0.45 | 0.57 | 0.90 |
| PI | 1.15 | 1.15 | 1.15 | 1.15 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.17 | 1.17 | 1.17 | 1.17 |
| 46 | TC | 2.71 | 2.73 | 2.76 | 2.79 | 2.90 | 2.90 | 2.93 | 2.96 | 2.99 | 2.99 | 2.99 | 3.02 | 3.25 | 3.25 | 3.25 | 3.25 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.65 | 0.79 | 0.92 | 1.00 | 0.56 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.57 | 0.92 |
| PI | 1.28 | 1.28 | 1.28 | 1.28 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.30 | 1.30 | 1.30 | 1.30 |
| 50 | TC | 2.56 | 2.59 | 2.62 | 2.65 | 2.73 | 2.73 | 2.76 | 2.79 | 2.82 | 2.82 | 2.82 | 2.85 | 3.05 | 3.05 | 3.05 | 3.05 |
| S/T | 0.89 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.95 | 1.00 | 0.56 | 0.70 | 0.85 | 0.98 | 0.32 | 0.46 | 0.59 | 0.97 |
| PI | 1.39 | 1.39 | 1.39 | 1.39 | 1.40 | 1.40 | 1.40 | 1.40 | 1.40 | 1.40 | 1.40 | 1.40 | 1.41 | 1.41 | 1.41 | 1.41 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS018D8S-1+38QUS018D8S-1 | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 515 | -15 | TC | 5.50 | 5.50 | 5.50 | 5.50 | 5.78 | 5.90 | 5.90 | 5.90 | 5.93 | 5.93 | 5.93 | 5.93 | 6.28 | 6.28 | 6.28 | 6.28 |
| S/T | 0.66 | 0.72 | 0.79 | 0.85 | 0.55 | 0.61 | 0.67 | 0.72 | 0.49 | 0.55 | 0.61 | 0.67 | 0.38 | 0.42 | 0.48 | 0.54 |
| PI | 1.02 | 1.02 | 1.02 | 1.02 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 1.02 |
| -10 | TC | 5.46 | 5.47 | 5.47 | 5.47 | 5.75 | 5.87 | 5.87 | 5.87 | 5.90 | 5.90 | 5.90 | 5.90 | 6.25 | 6.25 | 6.25 | 6.25 |
| S/T | 0.66 | 0.73 | 0.80 | 0.85 | 0.55 | 0.61 | 0.67 | 0.73 | 0.49 | 0.55 | 0.61 | 0.67 | 0.38 | 0.43 | 0.49 | 0.54 |
| PI | 1.01 | 1.02 | 1.02 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 1.02 |
| -5 | TC | 5.43 | 5.43 | 5.43 | 5.43 | 5.73 | 5.85 | 5.85 | 5.85 | 5.88 | 5.88 | 5.88 | 5.88 | 6.24 | 6.24 | 6.24 | 6.24 |
| S/T | 0.66 | 0.73 | 0.80 | 0.86 | 0.56 | 0.61 | 0.67 | 0.73 | 0.50 | 0.56 | 0.61 | 0.67 | 0.38 | 0.43 | 0.49 | 0.55 |
| PI | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 1.02 |
| 0 | TC | 5.40 | 5.41 | 5.41 | 5.41 | 5.71 | 5.83 | 5.83 | 5.83 | 5.87 | 5.87 | 5.87 | 5.87 | 6.23 | 6.23 | 6.23 | 6.23 |
| S/T | 0.67 | 0.74 | 0.80 | 0.86 | 0.56 | 0.62 | 0.68 | 0.74 | 0.50 | 0.56 | 0.62 | 0.68 | 0.38 | 0.43 | 0.49 | 0.55 |
| PI | 1.02 | 1.02 | 1.02 | 1.02 | 1.01 | 1.01 | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 |
| 5 | TC | 5.38 | 5.38 | 5.38 | 5.38 | 5.68 | 5.80 | 5.80 | 5.80 | 5.85 | 5.85 | 5.85 | 5.85 | 6.23 | 6.23 | 6.23 | 6.23 |
| S/T | 0.67 | 0.74 | 0.81 | 0.87 | 0.56 | 0.62 | 0.68 | 0.74 | 0.50 | 0.56 | 0.62 | 0.68 | 0.38 | 0.43 | 0.49 | 0.55 |
| PI | 1.03 | 1.03 | 1.03 | 1.03 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.03 | 1.03 | 1.03 | 1.03 |
| 10 | TC | 5.34 | 5.35 | 5.35 | 5.35 | 5.66 | 5.78 | 5.78 | 5.78 | 5.82 | 5.82 | 5.82 | 5.82 | 6.21 | 6.21 | 6.21 | 6.21 |
| S/T | 0.67 | 0.74 | 0.81 | 0.87 | 0.56 | 0.62 | 0.68 | 0.74 | 0.50 | 0.56 | 0.62 | 0.68 | 0.39 | 0.44 | 0.50 | 0.55 |
| PI | 1.04 | 1.05 | 1.05 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 |
| 15 | TC | 5.30 | 5.30 | 5.30 | 5.30 | 5.62 | 5.74 | 5.74 | 5.74 | 5.79 | 5.79 | 5.79 | 5.79 | 6.19 | 6.19 | 6.19 | 6.19 |
| S/T | 0.68 | 0.75 | 0.82 | 0.88 | 0.57 | 0.63 | 0.69 | 0.75 | 0.51 | 0.57 | 0.63 | 0.69 | 0.39 | 0.44 | 0.50 | 0.56 |
| PI | 1.07 | 1.07 | 1.07 | 1.07 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.07 | 1.07 | 1.07 | 1.07 |
| 20 | TC | 5.24 | 5.24 | 5.24 | 5.24 | 5.56 | 5.56 | 5.56 | 5.56 | 5.73 | 5.73 | 5.73 | 5.73 | 6.13 | 6.13 | 6.13 | 6.13 |
| S/T | 0.68 | 0.75 | 0.82 | 0.88 | 0.57 | 0.63 | 0.69 | 0.75 | 0.51 | 0.57 | 0.63 | 0.69 | 0.39 | 0.44 | 0.50 | 0.56 |
| PI | 1.11 | 1.11 | 1.11 | 1.11 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 | 1.10 |
| 25 | TC | 4.99 | 4.99 | 4.99 | 5.04 | 5.30 | 5.30 | 5.30 | 5.30 | 5.47 | 5.47 | 5.47 | 5.47 | 5.87 | 5.87 | 5.87 | 5.87 |
| S/T | 0.69 | 0.76 | 0.83 | 0.89 | 0.57 | 0.63 | 0.70 | 0.76 | 0.51 | 0.58 | 0.64 | 0.70 | 0.38 | 0.44 | 0.50 | 0.56 |
| PI | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 |
| 30 | TC | 4.76 | 4.76 | 4.76 | 4.81 | 5.07 | 5.07 | 5.07 | 5.07 | 5.22 | 5.22 | 5.22 | 5.22 | 5.62 | 5.62 | 5.62 | 5.62 |
| S/T | 0.69 | 0.77 | 0.84 | 0.91 | 0.57 | 0.64 | 0.71 | 0.77 | 0.51 | 0.58 | 0.64 | 0.71 | 0.38 | 0.44 | 0.50 | 0.56 |
| PI | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 |
| 35 | TC | 4.53 | 4.53 | 4.53 | 4.59 | 4.81 | 4.81 | 4.81 | 4.81 | 4.96 | 4.96 | 5.04 | 4.96 | 5.36 | 5.36 | 5.36 | 5.36 |
| S/T | 0.70 | 0.78 | 0.85 | 0.92 | 0.57 | 0.64 | 0.71 | 0.79 | 0.51 | 0.58 | 0.65 | 0.72 | 0.37 | 0.44 | 0.50 | 0.57 |
| PI | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.47 | 1.47 | 1.47 | 1.47 | 1.48 | 1.48 | 1.48 | 1.48 |
| 40 | TC | 4.28 | 4.28 | 4.29 | 4.34 | 4.55 | 4.55 | 4.55 | 4.55 | 4.70 | 4.70 | 4.74 | 4.70 | 5.07 | 5.07 | 5.07 | 5.07 |
| S/T | 0.71 | 0.80 | 0.88 | 0.96 | 0.58 | 0.66 | 0.73 | 0.81 | 0.51 | 0.59 | 0.67 | 0.74 | 0.37 | 0.44 | 0.51 | 0.58 |
| PI | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.62 | 1.62 | 1.62 | 1.62 | 1.63 | 1.63 | 1.63 | 1.63 |
| 46 | TC | 3.97 | 3.97 | 4.00 | 4.02 | 4.22 | 4.22 | 4.22 | 4.22 | 4.37 | 4.37 | 4.37 | 4.37 | 4.71 | 4.71 | 4.71 | 4.71 |
| S/T | 0.72 | 0.81 | 0.89 | 0.98 | 0.58 | 0.66 | 0.74 | 0.83 | 0.51 | 0.59 | 0.67 | 0.75 | 0.36 | 0.44 | 0.51 | 0.58 |
| PI | 1.79 | 1.79 | 1.79 | 1.79 | 1.80 | 1.80 | 1.80 | 1.80 | 1.80 | 1.80 | 1.80 | 1.80 | 1.82 | 1.82 | 1.82 | 1.82 |
| 50 | TC | 3.71 | 3.71 | 3.74 | 3.77 | 3.97 | 3.97 | 3.97 | 3.97 | 4.11 | 4.11 | 4.11 | 4.11 | 4.45 | 4.45 | 4.45 | 4.45 |
| S/T | 0.73 | 0.83 | 0.92 | 1.00 | 0.59 | 0.67 | 0.76 | 0.85 | 0.52 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 1.94 | 1.94 | 1.94 | 1.94 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.97 | 1.97 | 1.97 | 1.97 |
| 706 | -15 | TC | 5.62 | 5.62 | 5.68 | 5.74 | 5.90 | 5.90 | 5.90 | 5.90 | 6.06 | 6.06 | 6.06 | 6.06 | 6.43 | 6.43 | 6.43 | 6.43 |
| S/T | 0.70 | 0.78 | 0.98 | 1.00 | 0.56 | 0.64 | 0.72 | 0.80 | 0.49 | 0.58 | 0.66 | 0.73 | 0.35 | 0.42 | 0.49 | 0.57 |
| PI | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 |
| -10 | TC | 5.59 | 5.59 | 5.65 | 5.71 | 5.87 | 5.87 | 5.87 | 5.87 | 6.03 | 6.03 | 6.03 | 6.03 | 6.40 | 6.40 | 6.40 | 6.40 |
| S/T | 0.70 | 0.79 | 0.99 | 1.00 | 0.56 | 0.64 | 0.73 | 0.81 | 0.49 | 0.58 | 0.66 | 0.74 | 0.35 | 0.43 | 0.49 | 0.57 |
| PI | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 |
| -5 | TC | 5.56 | 5.56 | 5.62 | 5.67 | 5.85 | 5.85 | 5.85 | 5.85 | 6.00 | 6.00 | 6.00 | 6.00 | 6.39 | 6.39 | 6.39 | 6.39 |
| S/T | 0.70 | 0.79 | 0.99 | 1.00 | 0.57 | 0.64 | 0.73 | 0.81 | 0.50 | 0.59 | 0.66 | 0.74 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 |
| 0 | TC | 5.53 | 5.53 | 5.59 | 5.65 | 5.83 | 5.83 | 5.83 | 5.83 | 5.99 | 5.99 | 5.99 | 5.99 | 6.38 | 6.38 | 6.38 | 6.38 |
| S/T | 0.71 | 0.79 | 1.00 | 1.00 | 0.57 | 0.65 | 0.74 | 0.81 | 0.50 | 0.59 | 0.67 | 0.74 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.03 | 1.03 | 1.03 | 1.03 | 1.04 | 1.04 | 1.04 | 1.04 |
| 5 | TC | 5.50 | 5.50 | 5.56 | 5.62 | 5.80 | 5.80 | 5.80 | 5.80 | 5.97 | 5.97 | 5.97 | 5.97 | 6.38 | 6.38 | 6.38 | 6.38 |
| S/T | 0.71 | 0.80 | 1.00 | 1.00 | 0.57 | 0.65 | 0.74 | 0.82 | 0.50 | 0.59 | 0.67 | 0.75 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.04 | 1.04 | 1.04 | 1.04 | 1.05 | 1.05 | 1.05 | 1.05 |
| 10 | TC | 5.47 | 5.47 | 5.53 | 5.58 | 5.78 | 5.78 | 5.78 | 5.78 | 5.94 | 5.94 | 5.94 | 5.94 | 6.36 | 6.36 | 6.36 | 6.36 |
| S/T | 0.71 | 0.80 | 1.00 | 1.00 | 0.57 | 0.65 | 0.74 | 0.82 | 0.50 | 0.59 | 0.67 | 0.75 | 0.36 | 0.44 | 0.50 | 0.58 |
| PI | 1.06 | 1.06 | 1.06 | 1.06 | 1.07 | 1.07 | 1.07 | 1.07 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 |
| 15 | TC | 5.42 | 5.42 | 5.48 | 5.54 | 5.74 | 5.74 | 5.74 | 5.74 | 5.91 | 5.91 | 5.91 | 5.91 | 6.33 | 6.33 | 6.33 | 6.33 |
| S/T | 0.72 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.75 | 0.83 | 0.51 | 0.60 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 1.09 | 1.09 | 1.09 | 1.09 | 1.09 | 1.09 | 1.09 | 1.09 | 1.08 | 1.08 | 1.08 | 1.08 | 1.09 | 1.09 | 1.09 | 1.09 |
| 20 | TC | 5.36 | 5.36 | 5.42 | 5.48 | 5.68 | 5.68 | 5.68 | 5.68 | 5.85 | 5.85 | 5.85 | 5.85 | 6.28 | 6.28 | 6.28 | 6.28 |
| S/T | 0.72 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.75 | 0.83 | 0.51 | 0.60 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 |
| 25 | TC | 5.10 | 5.10 | 5.16 | 5.22 | 5.42 | 5.42 | 5.42 | 5.42 | 5.59 | 5.59 | 5.59 | 5.59 | 6.02 | 6.02 | 6.02 | 6.02 |
| S/T | 0.73 | 0.83 | 0.91 | 1.00 | 0.59 | 0.67 | 0.76 | 0.85 | 0.52 | 0.60 | 0.69 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 |
| 30 | TC | 4.87 | 4.87 | 4.93 | 4.99 | 5.19 | 5.19 | 5.19 | 5.19 | 5.33 | 5.33 | 5.33 | 5.33 | 5.76 | 5.76 | 5.76 | 5.76 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.70 | 0.78 | 0.35 | 0.44 | 0.52 | 0.60 |
| PI | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.37 | 1.37 | 1.37 | 1.37 |
| 35 | TC | 4.62 | 4.62 | 4.67 | 4.73 | 4.93 | 4.93 | 4.93 | 4.93 | 5.07 | 5.07 | 5.16 | 5.07 | 5.48 | 5.48 | 5.48 | 5.48 |
| S/T | 0.76 | 0.86 | 0.96 | 1.00 | 0.60 | 0.69 | 0.79 | 0.88 | 0.52 | 0.61 | 0.70 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 |
| 40 | TC | 4.29 | 4.30 | 4.34 | 4.39 | 4.57 | 4.57 | 4.57 | 4.60 | 4.71 | 4.71 | 4.76 | 4.71 | 5.09 | 5.09 | 5.09 | 5.09 |
| S/T | 0.78 | 0.89 | 1.00 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.66 | 1.66 | 1.66 | 1.66 | 1.67 | 1.67 | 1.67 | 1.67 |
| 46 | TC | 3.98 | 4.01 | 4.03 | 4.06 | 4.23 | 4.23 | 4.23 | 4.29 | 4.37 | 4.37 | 4.37 | 4.37 | 4.74 | 4.74 | 4.74 | 4.74 |
| S/T | 0.79 | 0.91 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.94 | 0.53 | 0.64 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.83 | 1.83 | 1.83 | 1.83 | 1.84 | 1.84 | 1.84 | 1.84 | 1.85 | 1.85 | 1.85 | 1.85 | 1.86 | 1.86 | 1.86 | 1.86 |
| 50 | TC | 3.72 | 3.75 | 3.78 | 3.81 | 3.98 | 3.98 | 3.98 | 4.01 | 4.12 | 4.12 | 4.12 | 4.12 | 4.46 | 4.46 | 4.46 | 4.46 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 0.97 | 0.54 | 0.65 | 0.76 | 0.88 | 0.34 | 0.44 | 0.55 | 0.91 |
| PI | 1.99 | 1.99 | 1.99 | 1.99 | 2.00 | 2.00 | 2.00 | 2.00 | 2.00 | 2.00 | 2.00 | 2.00 | 2.02 | 2.02 | 2.02 | 2.02 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 911 | -15 | TC | 5.74 | 5.80 | 5.86 | 5.92 | 6.05 | 6.05 | 6.05 | 6.11 | 6.20 | 6.20 | 6.20 | 6.20 | 6.57 | 6.57 | 6.57 | 6.57 |
| S/T | 0.75 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.98 | 0.51 | 0.61 | 0.70 | 0.80 | 0.33 | 0.42 | 0.51 | 0.61 |
| PI | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.05 | 1.05 | 1.05 | 1.05 |
| -10 | TC | 5.71 | 5.77 | 5.83 | 5.89 | 6.02 | 6.02 | 6.02 | 6.08 | 6.17 | 6.17 | 6.17 | 6.17 | 6.55 | 6.55 | 6.55 | 6.55 |
| S/T | 0.76 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.98 | 0.51 | 0.61 | 0.71 | 0.81 | 0.33 | 0.43 | 0.51 | 0.61 |
| PI | 1.05 | 1.05 | 1.05 | 1.05 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.05 | 1.05 | 1.05 | 1.05 |
| -5 | TC | 5.67 | 5.73 | 5.79 | 5.85 | 6.00 | 6.00 | 6.00 | 6.06 | 6.15 | 6.15 | 6.15 | 6.15 | 6.53 | 6.53 | 6.53 | 6.53 |
| S/T | 0.76 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.99 | 0.52 | 0.61 | 0.71 | 0.81 | 0.33 | 0.43 | 0.52 | 0.61 |
| PI | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 |
| 0 | TC | 5.65 | 5.71 | 5.76 | 5.82 | 5.97 | 5.97 | 5.97 | 6.03 | 6.13 | 6.13 | 6.13 | 6.13 | 6.53 | 6.53 | 6.53 | 6.53 |
| S/T | 0.76 | 0.86 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.99 | 0.52 | 0.62 | 0.72 | 0.81 | 0.33 | 0.43 | 0.52 | 0.62 |
| PI | 1.05 | 1.05 | 1.05 | 1.05 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 |
| 5 | TC | 5.62 | 5.68 | 5.74 | 5.79 | 5.95 | 5.95 | 5.95 | 6.01 | 6.11 | 6.11 | 6.11 | 6.11 | 6.52 | 6.52 | 6.52 | 6.52 |
| S/T | 0.77 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.33 | 0.43 | 0.52 | 0.62 |
| PI | 1.06 | 1.06 | 1.06 | 1.06 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 |
| 10 | TC | 5.58 | 5.64 | 5.70 | 5.76 | 5.92 | 5.92 | 5.92 | 5.98 | 6.09 | 6.09 | 6.09 | 6.09 | 6.51 | 6.51 | 6.51 | 6.51 |
| S/T | 0.77 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.34 | 0.44 | 0.52 | 0.62 |
| PI | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.09 | 1.09 | 1.09 | 1.09 | 1.08 | 1.08 | 1.08 | 1.08 |
| 15 | TC | 5.54 | 5.60 | 5.65 | 5.71 | 5.88 | 5.88 | 5.88 | 5.94 | 6.05 | 6.05 | 6.05 | 6.05 | 6.48 | 6.48 | 6.48 | 6.48 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.10 | 1.10 | 1.10 | 1.10 |
| 20 | TC | 5.48 | 5.53 | 5.59 | 5.65 | 5.82 | 5.82 | 5.82 | 5.88 | 5.99 | 5.99 | 5.99 | 5.99 | 6.42 | 6.42 | 6.42 | 6.42 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.14 | 1.14 | 1.14 | 1.14 |
| 25 | TC | 5.22 | 5.28 | 5.33 | 5.39 | 5.56 | 5.56 | 5.56 | 5.62 | 5.73 | 5.73 | 5.73 | 5.73 | 6.16 | 6.16 | 6.16 | 6.16 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.94 | 0.53 | 0.64 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 |
| 30 | TC | 4.99 | 5.05 | 5.10 | 5.16 | 5.30 | 5.30 | 5.30 | 5.36 | 5.45 | 5.45 | 5.45 | 5.45 | 5.88 | 5.88 | 5.88 | 5.88 |
| S/T | 0.81 | 0.92 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.96 | 0.54 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.40 | 1.40 | 1.40 | 1.40 |
| 35 | TC | 4.73 | 4.79 | 4.85 | 4.90 | 5.05 | 5.05 | 5.05 | 5.10 | 5.19 | 5.19 | 5.28 | 5.33 | 5.59 | 5.59 | 5.59 | 5.59 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.53 | 1.53 | 1.53 | 1.53 | 1.54 | 1.54 | 1.54 | 1.54 |
| 40 | TC | 4.39 | 4.43 | 4.47 | 4.52 | 4.68 | 4.68 | 4.71 | 4.77 | 4.82 | 4.82 | 4.87 | 4.93 | 5.21 | 5.21 | 5.21 | 5.21 |
| S/T | 0.86 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.93 | 0.33 | 0.45 | 0.57 | 0.90 |
| PI | 1.68 | 1.68 | 1.68 | 1.68 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.71 | 1.71 | 1.71 | 1.71 |
| 46 | TC | 4.06 | 4.09 | 4.12 | 4.15 | 4.35 | 4.35 | 4.40 | 4.46 | 4.49 | 4.49 | 4.49 | 4.54 | 4.85 | 4.85 | 4.85 | 4.85 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.65 | 0.79 | 0.93 | 1.00 | 0.56 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.58 | 0.92 |
| PI | 1.87 | 1.87 | 1.87 | 1.87 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.90 | 1.90 | 1.90 | 1.90 |
| 50 | TC | 3.81 | 3.84 | 3.87 | 3.89 | 4.06 | 4.06 | 4.09 | 4.12 | 4.20 | 4.20 | 4.20 | 4.23 | 4.57 | 4.57 | 4.57 | 4.57 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.82 | 0.96 | 1.00 | 0.56 | 0.71 | 0.85 | 0.99 | 0.32 | 0.46 | 0.59 | 0.97 |
| PI | 2.03 | 2.03 | 2.03 | 2.03 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.06 | 2.06 | 2.06 | 2.06 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS024D8S+38QUS024D8S | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 825 | -15 | TC | 7.35 | 7.34 | 7.34 | 7.40 | 7.73 | 7.88 | 7.88 | 7.88 | 7.93 | 7.93 | 7.93 | 7.93 | 8.40 | 8.40 | 8.40 | 8.40 |
| S/T | 0.69 | 0.75 | 0.83 | 0.91 | 0.55 | 0.63 | 0.70 | 0.77 | 0.49 | 0.56 | 0.64 | 0.70 | 0.36 | 0.42 | 0.48 | 0.55 |
| PI | 1.46 | 1.47 | 1.47 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.45 | 1.45 | 1.45 | 1.45 |
| -10 | TC | 7.31 | 7.30 | 7.30 | 7.36 | 7.69 | 7.84 | 7.84 | 7.84 | 7.89 | 7.89 | 7.89 | 7.89 | 8.37 | 8.37 | 8.37 | 8.37 |
| S/T | 0.69 | 0.76 | 0.83 | 0.91 | 0.55 | 0.63 | 0.70 | 0.78 | 0.49 | 0.56 | 0.64 | 0.71 | 0.36 | 0.43 | 0.49 | 0.55 |
| PI | 1.46 | 1.46 | 1.46 | 1.46 | 1.45 | 1.45 | 1.45 | 1.45 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 |
| -5 | TC | 7.26 | 7.26 | 7.26 | 7.32 | 7.66 | 7.81 | 7.81 | 7.81 | 7.86 | 7.86 | 7.86 | 7.86 | 8.35 | 8.35 | 8.35 | 8.35 |
| S/T | 0.69 | 0.76 | 0.84 | 0.92 | 0.56 | 0.63 | 0.70 | 0.78 | 0.50 | 0.57 | 0.64 | 0.71 | 0.36 | 0.43 | 0.49 | 0.56 |
| PI | 1.45 | 1.46 | 1.46 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 |
| 0 | TC | 7.23 | 7.22 | 7.22 | 7.28 | 7.63 | 7.78 | 7.78 | 7.78 | 7.84 | 7.84 | 7.84 | 7.84 | 8.34 | 8.34 | 8.34 | 8.34 |
| S/T | 0.70 | 0.76 | 0.84 | 0.92 | 0.56 | 0.64 | 0.71 | 0.78 | 0.50 | 0.57 | 0.65 | 0.72 | 0.36 | 0.43 | 0.49 | 0.56 |
| PI | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 |
| 5 | TC | 7.19 | 7.18 | 7.18 | 7.24 | 7.60 | 7.75 | 7.75 | 7.75 | 7.82 | 7.82 | 7.82 | 7.82 | 8.34 | 8.34 | 8.34 | 8.34 |
| S/T | 0.70 | 0.77 | 0.85 | 0.93 | 0.56 | 0.64 | 0.71 | 0.79 | 0.50 | 0.57 | 0.65 | 0.72 | 0.36 | 0.43 | 0.49 | 0.56 |
| PI | 1.47 | 1.48 | 1.48 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 |
| 10 | TC | 7.15 | 7.14 | 7.14 | 7.20 | 7.56 | 7.71 | 7.71 | 7.71 | 7.79 | 7.79 | 7.79 | 7.79 | 8.31 | 8.31 | 8.31 | 8.31 |
| S/T | 0.70 | 0.77 | 0.85 | 0.93 | 0.56 | 0.64 | 0.71 | 0.79 | 0.50 | 0.57 | 0.65 | 0.72 | 0.37 | 0.44 | 0.50 | 0.56 |
| PI | 1.50 | 1.50 | 1.50 | 1.50 | 1.49 | 1.49 | 1.49 | 1.49 | 1.50 | 1.50 | 1.50 | 1.50 | 1.49 | 1.49 | 1.49 | 1.49 |
| 15 | TC | 7.09 | 7.08 | 7.08 | 7.14 | 7.51 | 7.66 | 7.66 | 7.66 | 7.74 | 7.74 | 7.74 | 7.74 | 8.28 | 8.28 | 8.28 | 8.28 |
| S/T | 0.71 | 0.78 | 0.86 | 0.94 | 0.57 | 0.64 | 0.72 | 0.80 | 0.51 | 0.58 | 0.66 | 0.73 | 0.37 | 0.44 | 0.50 | 0.57 |
| PI | 1.53 | 1.54 | 1.54 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.52 | 1.52 | 1.52 | 1.52 |
| 20 | TC | 7.01 | 7.00 | 7.00 | 7.06 | 7.43 | 7.43 | 7.43 | 7.43 | 7.66 | 7.66 | 7.66 | 7.66 | 8.21 | 8.21 | 8.21 | 8.21 |
| S/T | 0.71 | 0.78 | 0.86 | 0.94 | 0.57 | 0.65 | 0.72 | 0.80 | 0.51 | 0.58 | 0.66 | 0.73 | 0.37 | 0.44 | 0.50 | 0.57 |
| PI | 1.59 | 1.59 | 1.59 | 1.59 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.57 | 1.57 | 1.57 | 1.57 |
| 25 | TC | 6.69 | 6.69 | 6.69 | 6.74 | 7.09 | 7.09 | 7.09 | 7.09 | 7.32 | 7.32 | 7.32 | 7.32 | 7.86 | 7.86 | 7.86 | 7.86 |
| S/T | 0.71 | 0.79 | 0.88 | 0.96 | 0.58 | 0.65 | 0.73 | 0.81 | 0.51 | 0.59 | 0.66 | 0.74 | 0.37 | 0.44 | 0.51 | 0.58 |
| PI | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 |
| 30 | TC | 6.37 | 6.37 | 6.43 | 6.49 | 6.77 | 6.77 | 6.77 | 6.77 | 6.97 | 6.97 | 6.97 | 6.97 | 7.52 | 7.52 | 7.52 | 7.52 |
| S/T | 0.72 | 0.81 | 0.89 | 0.97 | 0.58 | 0.66 | 0.74 | 0.82 | 0.51 | 0.59 | 0.67 | 0.75 | 0.36 | 0.44 | 0.51 | 0.58 |
| PI | 1.91 | 1.91 | 1.91 | 1.91 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.93 | 1.93 | 1.93 | 1.93 |
| 35 | TC | 6.06 | 6.06 | 6.11 | 6.17 | 6.43 | 6.43 | 6.43 | 6.43 | 6.63 | 6.63 | 6.74 | 6.63 | 7.17 | 7.17 | 7.17 | 7.17 |
| S/T | 0.73 | 0.82 | 0.91 | 1.00 | 0.58 | 0.67 | 0.76 | 0.84 | 0.52 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 2.09 | 2.09 | 2.09 | 2.09 | 2.10 | 2.10 | 2.10 | 2.10 | 2.11 | 2.11 | 2.11 | 2.11 | 2.12 | 2.12 | 2.12 | 2.12 |
| 40 | TC | 5.66 | 5.66 | 5.71 | 5.77 | 6.01 | 6.01 | 6.01 | 6.04 | 6.21 | 6.21 | 6.28 | 6.21 | 6.72 | 6.72 | 6.72 | 6.72 |
| S/T | 0.75 | 0.85 | 0.95 | 1.00 | 0.59 | 0.69 | 0.78 | 0.88 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 2.31 | 2.31 | 2.31 | 2.31 | 2.32 | 2.32 | 2.32 | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | 2.34 | 2.34 | 2.34 | 2.34 |
| 46 | TC | 5.24 | 5.24 | 5.29 | 5.35 | 5.58 | 5.58 | 5.58 | 5.64 | 5.78 | 5.78 | 5.78 | 5.78 | 6.23 | 6.23 | 6.23 | 6.23 |
| S/T | 0.76 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.79 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.61 |
| PI | 2.57 | 2.57 | 2.57 | 2.57 | 2.58 | 2.58 | 2.58 | 2.58 | 2.59 | 2.59 | 2.59 | 2.59 | 2.61 | 2.61 | 2.61 | 2.61 |
| 50 | TC | 4.90 | 4.95 | 5.01 | 5.07 | 5.24 | 5.24 | 5.24 | 5.29 | 5.44 | 5.44 | 5.44 | 5.44 | 5.89 | 5.89 | 5.89 | 5.89 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 2.79 | 2.79 | 2.79 | 2.79 | 2.80 | 2.80 | 2.80 | 2.80 | 2.81 | 2.81 | 2.81 | 2.81 | 2.83 | 2.83 | 2.83 | 2.83 |
| 1035 | -15 | TC | 7.50 | 7.50 | 7.56 | 7.65 | 7.88 | 7.88 | 7.88 | 7.88 | 8.09 | 8.09 | 8.09 | 8.09 | 8.58 | 8.58 | 8.58 | 8.58 |
| S/T | 0.71 | 0.81 | 0.98 | 1.00 | 0.57 | 0.66 | 0.74 | 0.83 | 0.50 | 0.59 | 0.68 | 0.76 | 0.34 | 0.42 | 0.50 | 0.58 |
| PI | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.48 | 1.48 | 1.48 | 1.48 |
| -10 | TC | 7.45 | 7.45 | 7.51 | 7.60 | 7.84 | 7.84 | 7.84 | 7.84 | 8.05 | 8.05 | 8.05 | 8.05 | 8.55 | 8.55 | 8.55 | 8.55 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.57 | 0.66 | 0.75 | 0.83 | 0.50 | 0.59 | 0.68 | 0.77 | 0.34 | 0.43 | 0.50 | 0.58 |
| PI | 1.49 | 1.49 | 1.49 | 1.49 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 |
| -5 | TC | 7.41 | 7.41 | 7.47 | 7.56 | 7.81 | 7.81 | 7.81 | 7.81 | 8.02 | 8.02 | 8.02 | 8.02 | 8.53 | 8.53 | 8.53 | 8.53 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.68 | 0.77 | 0.34 | 0.43 | 0.51 | 0.59 |
| PI | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.49 | 1.49 | 1.49 | 1.49 |
| 0 | TC | 7.37 | 7.37 | 7.43 | 7.52 | 7.78 | 7.78 | 7.78 | 7.78 | 7.99 | 7.99 | 7.99 | 7.99 | 8.52 | 8.52 | 8.52 | 8.52 |
| S/T | 0.73 | 0.82 | 1.00 | 1.00 | 0.58 | 0.67 | 0.75 | 0.84 | 0.51 | 0.60 | 0.69 | 0.77 | 0.34 | 0.43 | 0.51 | 0.59 |
| PI | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 |
| 5 | TC | 7.33 | 7.33 | 7.39 | 7.48 | 7.75 | 7.75 | 7.75 | 7.75 | 7.97 | 7.97 | 7.97 | 7.97 | 8.51 | 8.51 | 8.51 | 8.51 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.69 | 0.78 | 0.34 | 0.43 | 0.51 | 0.59 |
| PI | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 | 1.50 |
| 10 | TC | 7.29 | 7.29 | 7.35 | 7.44 | 7.71 | 7.71 | 7.71 | 7.71 | 7.93 | 7.93 | 7.93 | 7.93 | 8.49 | 8.49 | 8.49 | 8.49 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.69 | 0.78 | 0.35 | 0.44 | 0.51 | 0.59 |
| PI | 1.53 | 1.53 | 1.53 | 1.53 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 |
| 15 | TC | 7.23 | 7.23 | 7.29 | 7.38 | 7.66 | 7.66 | 7.66 | 7.66 | 7.89 | 7.89 | 7.89 | 7.89 | 8.46 | 8.46 | 8.46 | 8.46 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.60 |
| PI | 1.57 | 1.57 | 1.57 | 1.57 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.55 | 1.55 | 1.55 | 1.55 |
| 20 | TC | 7.15 | 7.15 | 7.21 | 7.29 | 7.58 | 7.58 | 7.58 | 7.58 | 7.81 | 7.81 | 7.81 | 7.81 | 8.38 | 8.38 | 8.38 | 8.38 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.60 |
| PI | 1.62 | 1.62 | 1.62 | 1.62 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 1.60 | 1.60 | 1.60 | 1.60 |
| 25 | TC | 6.83 | 6.83 | 6.89 | 6.95 | 7.26 | 7.26 | 7.26 | 7.26 | 7.46 | 7.46 | 7.46 | 7.46 | 8.04 | 8.04 | 8.04 | 8.04 |
| S/T | 0.75 | 0.86 | 0.95 | 1.00 | 0.59 | 0.69 | 0.79 | 0.88 | 0.52 | 0.61 | 0.71 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 1.79 | 1.79 | 1.79 | 1.79 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.79 | 1.79 | 1.79 | 1.79 |
| 30 | TC | 6.52 | 6.52 | 6.57 | 6.63 | 6.92 | 6.92 | 6.92 | 6.98 | 7.12 | 7.12 | 7.12 | 7.12 | 7.69 | 7.69 | 7.69 | 7.69 |
| S/T | 0.77 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.82 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 |
| 35 | TC | 6.17 | 6.23 | 6.29 | 6.34 | 6.57 | 6.57 | 6.57 | 6.63 | 6.78 | 6.78 | 6.89 | 6.78 | 7.32 | 7.32 | 7.32 | 7.32 |
| S/T | 0.78 | 0.89 | 1.00 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 2.13 | 2.13 | 2.13 | 2.13 | 2.14 | 2.14 | 2.14 | 2.14 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 |
| 40 | TC | 5.83 | 5.89 | 5.95 | 6.00 | 6.21 | 6.21 | 6.21 | 6.26 | 6.41 | 6.41 | 6.47 | 6.43 | 6.93 | 6.93 | 6.93 | 6.93 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.96 | 0.54 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 2.35 | 2.35 | 2.35 | 2.35 | 2.36 | 2.36 | 2.36 | 2.36 | 2.37 | 2.37 | 2.37 | 2.37 | 2.38 | 2.38 | 2.38 | 2.38 |
| 46 | TC | 5.41 | 5.46 | 5.52 | 5.58 | 5.75 | 5.75 | 5.75 | 5.81 | 5.95 | 5.95 | 5.95 | 6.01 | 6.44 | 6.44 | 6.44 | 6.44 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.77 | 0.89 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 2.62 | 2.62 | 2.62 | 2.62 | 2.63 | 2.63 | 2.63 | 2.63 | 2.64 | 2.64 | 2.64 | 2.64 | 2.66 | 2.66 | 2.66 | 2.66 |
| 50 | TC | 5.06 | 5.12 | 5.18 | 5.23 | 5.41 | 5.41 | 5.46 | 5.52 | 5.61 | 5.61 | 5.61 | 5.67 | 6.07 | 6.07 | 6.07 | 6.07 |
| S/T | 0.84 | 0.98 | 1.00 | 1.00 | 0.64 | 0.77 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.91 |
| PI | 2.84 | 2.84 | 2.84 | 2.84 | 2.85 | 2.85 | 2.85 | 2.85 | 2.86 | 2.86 | 2.86 | 2.86 | 2.88 | 2.88 | 2.88 | 2.88 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1229 | -15 | TC | 7.68 | 7.77 | 7.86 | 7.95 | 8.06 | 8.06 | 8.06 | 8.15 | 8.26 | 8.26 | 8.26 | 8.26 | 8.79 | 8.79 | 8.79 | 8.79 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.98 | 0.51 | 0.61 | 0.70 | 0.81 | 0.33 | 0.42 | 0.52 | 0.61 |
| PI | 1.52 | 1.52 | 1.52 | 1.52 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 |
| -10 | TC | 7.63 | 7.72 | 7.81 | 7.90 | 8.02 | 8.02 | 8.02 | 8.10 | 8.22 | 8.22 | 8.22 | 8.22 | 8.76 | 8.76 | 8.76 | 8.76 |
| S/T | 0.76 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.98 | 0.51 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.52 | 0.61 |
| PI | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 |
| -5 | TC | 7.59 | 7.68 | 7.77 | 7.85 | 7.99 | 7.99 | 7.99 | 8.07 | 8.19 | 8.19 | 8.19 | 8.19 | 8.73 | 8.73 | 8.73 | 8.73 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.59 | 0.69 | 0.80 | 0.99 | 0.52 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.53 | 0.61 |
| PI | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 |
| 0 | TC | 7.55 | 7.64 | 7.73 | 7.82 | 7.96 | 7.96 | 7.96 | 8.04 | 8.17 | 8.17 | 8.17 | 8.17 | 8.73 | 8.73 | 8.73 | 8.73 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.99 | 0.52 | 0.62 | 0.72 | 0.82 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 1.52 | 1.52 | 1.52 | 1.52 | 1.51 | 1.51 | 1.51 | 1.51 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 |
| 5 | TC | 7.51 | 7.60 | 7.69 | 7.78 | 7.93 | 7.93 | 7.93 | 8.01 | 8.14 | 8.14 | 8.14 | 8.14 | 8.72 | 8.72 | 8.72 | 8.72 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.83 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 |
| 10 | TC | 7.47 | 7.55 | 7.64 | 7.73 | 7.89 | 7.89 | 7.89 | 7.98 | 8.11 | 8.11 | 8.11 | 8.11 | 8.70 | 8.70 | 8.70 | 8.70 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 1.00 | 0.52 | 0.62 | 0.72 | 0.83 | 0.34 | 0.44 | 0.53 | 0.62 |
| PI | 1.56 | 1.56 | 1.56 | 1.56 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 | 1.55 |
| 15 | TC | 7.40 | 7.49 | 7.58 | 7.67 | 7.83 | 7.83 | 7.83 | 7.92 | 8.06 | 8.06 | 8.06 | 8.06 | 8.66 | 8.66 | 8.66 | 8.66 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.58 | 1.58 | 1.58 | 1.58 |
| 20 | TC | 7.32 | 7.41 | 7.49 | 7.58 | 7.75 | 7.75 | 7.75 | 7.84 | 7.98 | 7.98 | 7.98 | 7.98 | 8.58 | 8.58 | 8.58 | 8.58 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 1.65 | 1.65 | 1.65 | 1.65 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.63 | 1.63 | 1.63 | 1.63 |
| 25 | TC | 6.98 | 7.03 | 7.09 | 7.15 | 7.41 | 7.41 | 7.41 | 7.49 | 7.64 | 7.64 | 7.64 | 7.64 | 8.21 | 8.21 | 8.21 | 8.21 |
| S/T | 0.79 | 0.91 | 1.00 | 1.00 | 0.62 | 0.73 | 0.84 | 0.94 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 |
| 30 | TC | 6.63 | 6.69 | 6.75 | 6.80 | 7.06 | 7.06 | 7.06 | 7.12 | 7.29 | 7.29 | 7.29 | 7.29 | 7.84 | 7.84 | 7.84 | 7.84 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 0.97 | 0.54 | 0.65 | 0.76 | 0.88 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 1.98 | 1.98 | 1.98 | 1.98 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 2.00 | 2.00 | 2.00 | 2.00 |
| 35 | TC | 6.32 | 6.37 | 6.43 | 6.49 | 6.72 | 6.72 | 6.72 | 6.78 | 6.92 | 6.92 | 7.03 | 7.09 | 7.46 | 7.46 | 7.46 | 7.46 |
| S/T | 0.83 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.88 | 1.00 | 0.54 | 0.66 | 0.77 | 0.89 | 0.34 | 0.45 | 0.56 | 0.67 |
| PI | 2.17 | 2.17 | 2.17 | 2.17 | 2.18 | 2.18 | 2.18 | 2.18 | 2.19 | 2.19 | 2.19 | 2.19 | 2.20 | 2.20 | 2.20 | 2.20 |
| 40 | TC | 5.96 | 6.02 | 6.08 | 6.13 | 6.35 | 6.35 | 6.38 | 6.43 | 6.54 | 6.54 | 6.60 | 6.66 | 7.07 | 7.07 | 7.07 | 7.07 |
| S/T | 0.86 | 1.00 | 1.00 | 1.00 | 0.65 | 0.78 | 0.92 | 1.00 | 0.55 | 0.68 | 0.81 | 0.94 | 0.33 | 0.45 | 0.57 | 0.90 |
| PI | 2.40 | 2.40 | 2.40 | 2.40 | 2.41 | 2.41 | 2.41 | 2.41 | 2.42 | 2.42 | 2.42 | 2.42 | 2.43 | 2.43 | 2.43 | 2.43 |
| 46 | TC | 5.52 | 5.58 | 5.64 | 5.69 | 5.90 | 5.90 | 5.95 | 6.01 | 6.07 | 6.07 | 6.07 | 6.13 | 6.59 | 6.59 | 6.59 | 6.59 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.83 | 0.96 | 0.33 | 0.45 | 0.58 | 0.92 |
| PI | 2.67 | 2.67 | 2.67 | 2.67 | 2.68 | 2.68 | 2.68 | 2.68 | 2.69 | 2.69 | 2.69 | 2.69 | 2.71 | 2.71 | 2.71 | 2.71 |
| 50 | TC | 5.18 | 5.23 | 5.29 | 5.35 | 5.52 | 5.52 | 5.58 | 5.64 | 5.72 | 5.72 | 5.72 | 5.78 | 6.18 | 6.18 | 6.18 | 6.18 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.82 | 0.97 | 1.00 | 0.57 | 0.71 | 0.85 | 0.99 | 0.32 | 0.46 | 0.59 | 0.97 |
| PI | 2.89 | 2.89 | 2.89 | 2.89 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.94 | 2.94 | 2.94 | 2.94 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS030D8S+38QUS030D8S | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1500 | -15 | TC | 9.20 | 9.31 | 9.40 | 9.49 | 9.68 | 9.89 | 9.98 | 10.07 | 9.90 | 9.90 | 9.90 | 9.90 | 10.52 | 10.52 | 10.52 | 10.52 |
| S/T | 0.76 | 0.87 | 0.97 | 0.97 | 0.59 | 0.69 | 0.80 | 0.90 | 0.51 | 0.61 | 0.71 | 0.82 | 0.33 | 0.42 | 0.52 | 0.62 |
| PI | 1.67 | 1.66 | 1.66 | 1.67 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.65 | 1.65 | 1.65 | 1.65 |
| -10 | TC | 9.15 | 9.25 | 9.34 | 9.43 | 9.62 | 9.83 | 9.92 | 10.01 | 9.85 | 9.85 | 9.85 | 9.85 | 10.49 | 10.49 | 10.49 | 10.49 |
| S/T | 0.77 | 0.87 | 0.97 | 0.97 | 0.59 | 0.70 | 0.81 | 0.90 | 0.51 | 0.61 | 0.72 | 0.82 | 0.33 | 0.43 | 0.52 | 0.62 |
| PI | 1.66 | 1.65 | 1.65 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 |
| -5 | TC | 9.09 | 9.20 | 9.29 | 9.38 | 9.59 | 9.80 | 9.89 | 9.98 | 9.82 | 9.82 | 9.82 | 9.82 | 10.46 | 10.46 | 10.46 | 10.46 |
| S/T | 0.77 | 0.88 | 0.98 | 0.98 | 0.59 | 0.70 | 0.81 | 0.91 | 0.52 | 0.61 | 0.72 | 0.83 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 1.65 | 1.65 | 1.65 | 1.65 | 1.66 | 1.66 | 1.66 | 1.66 | 1.65 | 1.65 | 1.65 | 1.65 | 1.66 | 1.66 | 1.66 | 1.66 |
| 0 | TC | 9.05 | 9.15 | 9.24 | 9.33 | 9.55 | 9.76 | 9.85 | 9.94 | 9.79 | 9.79 | 9.79 | 9.79 | 10.45 | 10.45 | 10.45 | 10.45 |
| S/T | 0.77 | 0.88 | 0.98 | 0.98 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.73 | 0.83 | 0.33 | 0.43 | 0.53 | 0.63 |
| PI | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 |
| 5 | TC | 9.00 | 9.11 | 9.19 | 9.28 | 9.51 | 9.72 | 9.81 | 9.90 | 9.76 | 9.76 | 9.76 | 9.76 | 10.44 | 10.44 | 10.44 | 10.44 |
| S/T | 0.78 | 0.89 | 0.99 | 0.99 | 0.60 | 0.71 | 0.82 | 0.92 | 0.52 | 0.62 | 0.73 | 0.84 | 0.33 | 0.43 | 0.53 | 0.63 |
| PI | 1.68 | 1.67 | 1.67 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 |
| 10 | TC | 8.95 | 9.05 | 9.14 | 9.23 | 9.47 | 9.68 | 9.77 | 9.85 | 9.72 | 9.72 | 9.72 | 9.72 | 10.42 | 10.42 | 10.42 | 10.42 |
| S/T | 0.78 | 0.89 | 0.99 | 0.99 | 0.60 | 0.71 | 0.82 | 0.92 | 0.52 | 0.62 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 |
| 15 | TC | 8.87 | 8.98 | 9.06 | 9.15 | 9.41 | 9.61 | 9.70 | 9.79 | 9.66 | 9.66 | 9.66 | 9.66 | 10.37 | 10.37 | 10.37 | 10.37 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.93 | 0.53 | 0.63 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.75 | 1.74 | 1.74 | 1.75 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.73 | 1.73 | 1.73 | 1.73 |
| 20 | TC | 8.77 | 8.88 | 8.96 | 9.05 | 9.31 | 9.31 | 9.31 | 9.39 | 9.56 | 9.56 | 9.56 | 9.56 | 10.28 | 10.28 | 10.28 | 10.28 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.93 | 0.53 | 0.63 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 1.81 | 1.80 | 1.80 | 1.81 | 1.80 | 1.80 | 1.80 | 1.80 | 1.79 | 1.79 | 1.79 | 1.79 | 1.78 | 1.78 | 1.78 | 1.78 |
| 25 | TC | 8.36 | 8.44 | 8.53 | 8.62 | 8.90 | 8.90 | 8.90 | 8.99 | 9.16 | 9.16 | 9.16 | 9.16 | 9.85 | 9.85 | 9.85 | 9.85 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.84 | 0.95 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 |
| 30 | TC | 7.98 | 8.07 | 8.16 | 8.24 | 8.47 | 8.47 | 8.47 | 8.56 | 8.73 | 8.73 | 8.73 | 8.73 | 9.42 | 9.42 | 9.42 | 9.42 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.63 | 0.74 | 0.86 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 2.18 | 2.18 | 2.18 | 2.18 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.20 | 2.20 | 2.20 | 2.20 |
| 35 | TC | 7.58 | 7.67 | 7.75 | 7.84 | 8.07 | 8.07 | 8.07 | 8.16 | 8.33 | 8.33 | 8.44 | 8.53 | 8.96 | 8.96 | 8.96 | 8.96 |
| S/T | 0.83 | 0.96 | 1.00 | 1.00 | 0.63 | 0.76 | 0.88 | 1.00 | 0.54 | 0.66 | 0.78 | 0.89 | 0.33 | 0.45 | 0.56 | 0.67 |
| PI | 2.38 | 2.38 | 2.38 | 2.38 | 2.39 | 2.39 | 2.39 | 2.39 | 2.40 | 2.40 | 2.40 | 2.40 | 2.41 | 2.41 | 2.41 | 2.41 |
| 40 | TC | 7.04 | 7.11 | 7.18 | 7.25 | 7.51 | 7.51 | 7.53 | 7.60 | 7.73 | 7.73 | 7.80 | 7.88 | 8.34 | 8.34 | 8.34 | 8.34 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.65 | 0.79 | 0.92 | 1.00 | 0.55 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.57 | 0.70 |
| PI | 2.63 | 2.63 | 2.63 | 2.63 | 2.64 | 2.64 | 2.64 | 2.64 | 2.65 | 2.65 | 2.65 | 2.65 | 2.67 | 2.67 | 2.67 | 2.67 |
| 46 | TC | 6.51 | 6.57 | 6.63 | 6.68 | 6.96 | 6.96 | 7.02 | 7.08 | 7.16 | 7.16 | 7.16 | 7.25 | 7.76 | 7.76 | 7.76 | 7.76 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.94 | 1.00 | 0.56 | 0.70 | 0.84 | 0.97 | 0.33 | 0.45 | 0.58 | 0.71 |
| PI | 2.93 | 2.93 | 2.93 | 2.93 | 2.94 | 2.94 | 2.94 | 2.94 | 2.95 | 2.95 | 2.95 | 2.95 | 2.97 | 2.97 | 2.97 | 2.97 |
| 50 | TC | 6.12 | 6.17 | 6.23 | 6.29 | 6.54 | 6.54 | 6.60 | 6.65 | 6.74 | 6.74 | 6.74 | 6.80 | 7.30 | 7.30 | 7.30 | 7.30 |
| S/T | 0.91 | 1.00 | 1.00 | 1.00 | 0.68 | 0.83 | 0.98 | 1.00 | 0.57 | 0.72 | 0.86 | 1.00 | 0.32 | 0.46 | 0.59 | 0.73 |
| PI | 3.17 | 3.17 | 3.17 | 3.17 | 3.19 | 3.19 | 3.19 | 3.19 | 3.20 | 3.20 | 3.20 | 3.20 | 3.22 | 3.22 | 3.22 | 3.22 |
| 1800 | -15 | TC | 9.40 | 9.49 | 9.58 | 9.67 | 9.89 | 9.89 | 9.98 | 10.07 | 10.12 | 10.12 | 10.12 | 10.20 | 10.76 | 10.76 | 10.76 | 10.76 |
| S/T | 0.81 | 0.94 | 0.98 | 1.00 | 0.62 | 0.73 | 0.86 | 0.97 | 0.53 | 0.65 | 0.76 | 0.88 | 0.32 | 0.43 | 0.54 | 0.66 |
| PI | 1.70 | 1.70 | 1.70 | 1.70 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 |
| -10 | TC | 9.35 | 9.44 | 9.53 | 9.62 | 9.83 | 9.83 | 9.92 | 10.01 | 10.06 | 10.06 | 10.06 | 10.15 | 10.73 | 10.73 | 10.73 | 10.73 |
| S/T | 0.82 | 0.94 | 0.99 | 1.00 | 0.62 | 0.74 | 0.86 | 0.97 | 0.53 | 0.65 | 0.77 | 0.88 | 0.32 | 0.44 | 0.54 | 0.66 |
| PI | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 |
| -5 | TC | 9.29 | 9.38 | 9.47 | 9.56 | 9.80 | 9.80 | 9.89 | 9.98 | 10.03 | 10.03 | 10.03 | 10.12 | 10.70 | 10.70 | 10.70 | 10.70 |
| S/T | 0.82 | 0.95 | 0.99 | 1.00 | 0.62 | 0.74 | 0.87 | 0.98 | 0.54 | 0.65 | 0.77 | 0.89 | 0.32 | 0.44 | 0.55 | 0.66 |
| PI | 1.69 | 1.69 | 1.69 | 1.69 | 1.68 | 1.68 | 1.68 | 1.68 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 |
| 0 | TC | 9.24 | 9.33 | 9.42 | 9.51 | 9.76 | 9.76 | 9.85 | 9.94 | 10.00 | 10.00 | 10.00 | 10.09 | 10.69 | 10.69 | 10.69 | 10.69 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.74 | 0.87 | 0.98 | 0.54 | 0.66 | 0.77 | 0.89 | 0.32 | 0.44 | 0.55 | 0.67 |
| PI | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 | 1.70 |
| 5 | TC | 9.20 | 9.29 | 9.37 | 9.46 | 9.72 | 9.72 | 9.81 | 9.90 | 9.97 | 9.97 | 9.97 | 10.06 | 10.68 | 10.68 | 10.68 | 10.68 |
| S/T | 0.83 | 0.96 | 1.00 | 1.00 | 0.63 | 0.75 | 0.88 | 0.99 | 0.54 | 0.66 | 0.78 | 0.90 | 0.33 | 0.44 | 0.55 | 0.67 |
| PI | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 |
| 10 | TC | 9.14 | 9.23 | 9.32 | 9.41 | 9.68 | 9.68 | 9.77 | 9.85 | 9.93 | 9.93 | 9.93 | 10.01 | 10.65 | 10.65 | 10.65 | 10.65 |
| S/T | 0.83 | 0.96 | 1.00 | 1.00 | 0.63 | 0.75 | 0.88 | 0.99 | 0.54 | 0.66 | 0.78 | 0.90 | 0.33 | 0.45 | 0.55 | 0.67 |
| PI | 1.74 | 1.74 | 1.74 | 1.74 | 1.73 | 1.73 | 1.73 | 1.73 | 1.74 | 1.74 | 1.74 | 1.74 | 1.73 | 1.73 | 1.73 | 1.73 |
| 15 | TC | 9.07 | 9.15 | 9.24 | 9.33 | 9.61 | 9.61 | 9.70 | 9.79 | 9.87 | 9.87 | 9.87 | 9.95 | 10.61 | 10.61 | 10.61 | 10.61 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.68 |
| PI | 1.78 | 1.78 | 1.78 | 1.78 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 |
| 20 | TC | 8.96 | 9.05 | 9.14 | 9.22 | 9.51 | 9.51 | 9.60 | 9.68 | 9.77 | 9.77 | 9.77 | 9.86 | 10.52 | 10.52 | 10.52 | 10.52 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.68 |
| PI | 1.84 | 1.84 | 1.84 | 1.84 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.82 | 1.82 | 1.82 | 1.82 |
| 25 | TC | 8.53 | 8.62 | 8.71 | 8.79 | 9.08 | 9.08 | 9.17 | 9.25 | 9.34 | 9.34 | 9.34 | 9.42 | 10.06 | 10.06 | 10.06 | 10.06 |
| S/T | 0.86 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.93 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 |
| 30 | TC | 8.13 | 8.22 | 8.30 | 8.39 | 8.65 | 8.65 | 8.74 | 8.82 | 8.91 | 8.91 | 8.91 | 8.99 | 9.63 | 9.63 | 9.63 | 9.63 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.83 | 0.96 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.24 | 2.24 | 2.24 | 2.24 | 2.25 | 2.25 | 2.25 | 2.25 |
| 35 | TC | 7.73 | 7.82 | 7.90 | 7.99 | 8.25 | 8.25 | 8.33 | 8.42 | 8.48 | 8.48 | 8.62 | 8.71 | 9.17 | 9.17 | 9.17 | 9.17 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.96 | 1.00 | 0.56 | 0.71 | 0.84 | 0.98 | 0.32 | 0.46 | 0.59 | 0.72 |
| PI | 2.43 | 2.43 | 2.43 | 2.43 | 2.44 | 2.44 | 2.44 | 2.44 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 |
| 40 | TC | 7.29 | 7.37 | 7.44 | 7.51 | 7.79 | 7.79 | 7.87 | 7.96 | 8.02 | 8.02 | 8.13 | 8.22 | 8.67 | 8.67 | 8.67 | 8.67 |
| S/T | 0.94 | 1.00 | 1.00 | 1.00 | 0.69 | 0.85 | 1.00 | 1.00 | 0.58 | 0.73 | 0.89 | 1.00 | 0.32 | 0.46 | 0.61 | 0.75 |
| PI | 2.69 | 2.69 | 2.69 | 2.69 | 2.70 | 2.70 | 2.70 | 2.70 | 2.71 | 2.71 | 2.71 | 2.71 | 2.72 | 2.72 | 2.72 | 2.72 |
| 46 | TC | 6.76 | 6.82 | 6.87 | 6.93 | 7.22 | 7.22 | 7.31 | 7.39 | 7.45 | 7.45 | 7.54 | 7.62 | 8.05 | 8.05 | 8.05 | 8.05 |
| S/T | 0.96 | 1.00 | 1.00 | 1.00 | 0.70 | 0.87 | 1.00 | 1.00 | 0.58 | 0.75 | 0.90 | 1.00 | 0.32 | 0.47 | 0.62 | 0.77 |
| PI | 2.99 | 2.99 | 2.99 | 2.99 | 3.00 | 3.00 | 3.00 | 3.00 | 3.01 | 3.01 | 3.01 | 3.01 | 3.03 | 3.03 | 3.03 | 3.03 |
| 50 | TC | 6.33 | 6.39 | 6.44 | 6.50 | 6.76 | 6.82 | 6.87 | 6.93 | 6.99 | 6.99 | 7.05 | 7.11 | 7.59 | 7.59 | 7.59 | 7.59 |
| S/T | 0.99 | 1.00 | 1.00 | 1.00 | 0.72 | 0.90 | 1.00 | 1.00 | 0.60 | 0.77 | 0.94 | 1.00 | 0.31 | 0.47 | 0.63 | 0.91 |
| PI | 3.24 | 3.24 | 3.24 | 3.24 | 3.25 | 3.25 | 3.25 | 3.25 | 3.26 | 3.26 | 3.26 | 3.26 | 3.29 | 3.29 | 3.29 | 3.29 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2100 | -15 | TC | 9.58 | 9.67 | 9.76 | 9.85 | 10.07 | 10.07 | 10.16 | 10.25 | 10.32 | 10.32 | 10.32 | 10.41 | 10.97 | 10.97 | 10.97 | 10.97 |
| S/T | 0.86 | 0.97 | 1.00 | 1.00 | 0.65 | 0.78 | 0.92 | 0.98 | 0.54 | 0.68 | 0.82 | 0.95 | 0.31 | 0.44 | 0.57 | 0.70 |
| PI | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.72 | 1.72 | 1.72 | 1.72 |
| -10 | TC | 9.53 | 9.62 | 9.71 | 9.80 | 10.01 | 10.01 | 10.10 | 10.19 | 10.27 | 10.27 | 10.27 | 10.36 | 10.93 | 10.93 | 10.93 | 10.93 |
| S/T | 0.86 | 0.97 | 1.00 | 1.00 | 0.65 | 0.79 | 0.92 | 0.98 | 0.54 | 0.68 | 0.82 | 0.95 | 0.31 | 0.45 | 0.57 | 0.70 |
| PI | 1.73 | 1.73 | 1.73 | 1.73 | 1.72 | 1.72 | 1.72 | 1.72 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 |
| -5 | TC | 9.47 | 9.56 | 9.65 | 9.74 | 9.98 | 9.98 | 10.06 | 10.15 | 10.23 | 10.23 | 10.23 | 10.32 | 10.90 | 10.90 | 10.90 | 10.90 |
| S/T | 0.87 | 0.98 | 1.00 | 1.00 | 0.65 | 0.79 | 0.93 | 0.99 | 0.55 | 0.68 | 0.83 | 0.96 | 0.31 | 0.45 | 0.58 | 0.70 |
| PI | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 |
| 0 | TC | 9.42 | 9.51 | 9.60 | 9.69 | 9.94 | 9.94 | 10.03 | 10.11 | 10.21 | 10.21 | 10.21 | 10.29 | 10.89 | 10.89 | 10.89 | 10.89 |
| S/T | 0.87 | 0.98 | 1.00 | 1.00 | 0.66 | 0.79 | 0.93 | 0.99 | 0.55 | 0.69 | 0.83 | 0.96 | 0.31 | 0.45 | 0.58 | 0.71 |
| PI | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.74 | 1.74 | 1.74 | 1.74 |
| 5 | TC | 9.37 | 9.46 | 9.55 | 9.64 | 9.90 | 9.90 | 9.99 | 10.08 | 10.17 | 10.17 | 10.17 | 10.26 | 10.88 | 10.88 | 10.88 | 10.88 |
| S/T | 0.88 | 0.99 | 1.00 | 1.00 | 0.66 | 0.80 | 0.94 | 1.00 | 0.55 | 0.69 | 0.84 | 0.97 | 0.32 | 0.45 | 0.58 | 0.71 |
| PI | 1.75 | 1.75 | 1.75 | 1.75 | 1.74 | 1.74 | 1.74 | 1.74 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 |
| 10 | TC | 9.32 | 9.41 | 9.49 | 9.58 | 9.85 | 9.85 | 9.94 | 10.03 | 10.13 | 10.13 | 10.13 | 10.22 | 10.86 | 10.86 | 10.86 | 10.86 |
| S/T | 0.88 | 0.99 | 1.00 | 1.00 | 0.66 | 0.80 | 0.94 | 1.00 | 0.55 | 0.69 | 0.84 | 0.97 | 0.32 | 0.46 | 0.58 | 0.71 |
| PI | 1.78 | 1.78 | 1.78 | 1.78 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 |
| 15 | TC | 9.24 | 9.33 | 9.42 | 9.50 | 9.79 | 9.79 | 9.87 | 9.96 | 10.07 | 10.07 | 10.07 | 10.16 | 10.81 | 10.81 | 10.81 | 10.81 |
| S/T | 0.89 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.95 | 1.00 | 0.56 | 0.70 | 0.85 | 0.98 | 0.32 | 0.46 | 0.59 | 0.72 |
| PI | 1.82 | 1.82 | 1.82 | 1.82 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 | 1.81 |
| 20 | TC | 9.14 | 9.22 | 9.31 | 9.40 | 9.68 | 9.68 | 9.77 | 9.86 | 9.97 | 9.97 | 9.97 | 10.06 | 10.72 | 10.72 | 10.72 | 10.72 |
| S/T | 0.89 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.95 | 1.00 | 0.56 | 0.70 | 0.85 | 0.98 | 0.32 | 0.46 | 0.59 | 0.72 |
| PI | 1.88 | 1.88 | 1.88 | 1.88 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.86 | 1.86 | 1.86 | 1.86 |
| 25 | TC | 8.71 | 8.79 | 8.88 | 8.96 | 9.25 | 9.25 | 9.34 | 9.42 | 9.54 | 9.54 | 9.54 | 9.63 | 10.26 | 10.26 | 10.26 | 10.26 |
| S/T | 0.91 | 1.00 | 1.00 | 1.00 | 0.68 | 0.83 | 0.98 | 1.00 | 0.57 | 0.72 | 0.86 | 1.00 | 0.32 | 0.46 | 0.60 | 0.73 |
| PI | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 |
| 30 | TC | 8.30 | 8.39 | 8.48 | 8.56 | 8.82 | 8.82 | 8.91 | 8.99 | 9.11 | 9.11 | 9.19 | 9.28 | 9.80 | 9.80 | 9.80 | 9.80 |
| S/T | 0.93 | 1.00 | 1.00 | 1.00 | 0.69 | 0.85 | 1.00 | 1.00 | 0.58 | 0.73 | 0.88 | 1.00 | 0.32 | 0.46 | 0.61 | 0.75 |
| PI | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.28 | 2.28 | 2.28 | 2.28 |
| 35 | TC | 7.90 | 7.99 | 8.07 | 8.16 | 8.39 | 8.39 | 8.48 | 8.56 | 8.65 | 8.65 | 8.79 | 8.88 | 9.34 | 9.34 | 9.34 | 9.34 |
| S/T | 0.96 | 1.00 | 1.00 | 1.00 | 0.70 | 0.87 | 1.00 | 1.00 | 0.58 | 0.75 | 0.90 | 1.00 | 0.32 | 0.47 | 0.62 | 0.77 |
| PI | 2.48 | 2.48 | 2.48 | 2.48 | 2.49 | 2.49 | 2.49 | 2.49 | 2.50 | 2.50 | 2.50 | 2.50 | 2.51 | 2.51 | 2.51 | 2.51 |
| 40 | TC | 7.44 | 7.51 | 7.59 | 7.66 | 7.93 | 7.97 | 8.05 | 8.14 | 8.17 | 8.17 | 8.29 | 8.38 | 8.84 | 8.84 | 8.84 | 8.84 |
| S/T | 1.00 | 1.00 | 1.00 | 1.00 | 0.73 | 0.91 | 1.00 | 1.00 | 0.60 | 0.78 | 0.95 | 1.00 | 0.31 | 0.48 | 0.64 | 0.90 |
| PI | 2.74 | 2.74 | 2.74 | 2.74 | 2.75 | 2.75 | 2.75 | 2.75 | 2.76 | 2.76 | 2.76 | 2.76 | 2.78 | 2.78 | 2.78 | 2.78 |
| 46 | TC | 6.87 | 6.93 | 6.99 | 7.05 | 7.36 | 7.45 | 7.54 | 7.62 | 7.59 | 7.59 | 7.68 | 7.77 | 8.23 | 8.23 | 8.23 | 8.23 |
| S/T | 1.00 | 1.00 | 1.00 | 1.00 | 0.74 | 0.93 | 1.00 | 1.00 | 0.61 | 0.80 | 0.98 | 1.00 | 0.31 | 0.48 | 0.65 | 0.92 |
| PI | 3.05 | 3.05 | 3.05 | 3.05 | 3.06 | 3.06 | 3.06 | 3.06 | 3.07 | 3.07 | 3.07 | 3.07 | 3.10 | 3.10 | 3.10 | 3.10 |
| 50 | TC | 6.47 | 6.53 | 6.59 | 6.64 | 6.90 | 6.96 | 7.02 | 7.08 | 7.13 | 7.13 | 7.19 | 7.28 | 7.74 | 7.74 | 7.74 | 7.74 |
| S/T | 1.00 | 1.00 | 1.00 | 1.00 | 0.76 | 0.96 | 1.00 | 1.00 | 0.62 | 0.82 | 1.00 | 1.00 | 0.30 | 0.49 | 0.67 | 0.97 |
| PI | 3.31 | 3.31 | 3.31 | 3.31 | 3.32 | 3.32 | 3.32 | 3.32 | 3.33 | 3.33 | 3.33 | 3.33 | 3.35 | 3.35 | 3.35 | 3.35 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS036D8S+38QUS036D8S | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1500 | -15 | TC | 11.05 | 11.06 | 11.18 | 11.30 | 11.63 | 11.87 | 11.87 | 11.99 | 11.90 | 11.90 | 11.90 | 11.90 | 12.65 | 12.65 | 12.65 | 12.65 |
| S/T | 0.71 | 0.81 | 0.90 | 0.97 | 0.57 | 0.65 | 0.74 | 0.83 | 0.50 | 0.59 | 0.67 | 0.75 | 0.35 | 0.42 | 0.50 | 0.58 |
| PI | 2.63 | 2.63 | 2.63 | 2.63 | 2.62 | 2.62 | 2.62 | 2.62 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 |
| -10 | TC | 10.99 | 11.00 | 11.11 | 11.23 | 11.56 | 11.80 | 11.80 | 11.92 | 11.84 | 11.84 | 11.84 | 11.84 | 12.60 | 12.60 | 12.60 | 12.60 |
| S/T | 0.72 | 0.82 | 0.90 | 0.97 | 0.57 | 0.66 | 0.75 | 0.83 | 0.50 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 2.62 | 2.61 | 2.61 | 2.62 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.62 | 2.62 | 2.62 | 2.62 |
| -5 | TC | 10.92 | 10.93 | 11.05 | 11.17 | 11.52 | 11.76 | 11.76 | 11.88 | 11.80 | 11.80 | 11.80 | 11.80 | 12.57 | 12.57 | 12.57 | 12.57 |
| S/T | 0.72 | 0.82 | 0.91 | 0.98 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.62 | 2.62 | 2.62 | 2.62 |
| 0 | TC | 10.87 | 10.87 | 10.99 | 11.11 | 11.47 | 11.71 | 11.71 | 11.83 | 11.77 | 11.77 | 11.77 | 11.77 | 12.56 | 12.56 | 12.56 | 12.56 |
| S/T | 0.73 | 0.82 | 0.91 | 0.98 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.60 | 0.68 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.63 | 2.63 | 2.63 | 2.63 |
| 5 | TC | 10.81 | 10.82 | 10.94 | 11.06 | 11.43 | 11.67 | 11.67 | 11.79 | 11.73 | 11.73 | 11.73 | 11.73 | 12.55 | 12.55 | 12.55 | 12.55 |
| S/T | 0.73 | 0.83 | 0.92 | 0.99 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.65 | 2.64 | 2.64 | 2.65 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.65 | 2.65 | 2.65 | 2.65 |
| 10 | TC | 10.75 | 10.75 | 10.87 | 10.99 | 11.38 | 11.61 | 11.61 | 11.73 | 11.68 | 11.68 | 11.68 | 11.68 | 12.52 | 12.52 | 12.52 | 12.52 |
| S/T | 0.73 | 0.83 | 0.92 | 0.99 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 2.69 | 2.69 | 2.69 | 2.69 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 |
| 15 | TC | 10.66 | 10.67 | 10.78 | 10.90 | 11.30 | 11.54 | 11.54 | 11.65 | 11.61 | 11.61 | 11.61 | 11.61 | 12.46 | 12.46 | 12.46 | 12.46 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.67 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 2.76 | 2.75 | 2.75 | 2.76 | 2.75 | 2.75 | 2.75 | 2.75 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 |
| 20 | TC | 10.54 | 10.55 | 10.66 | 10.78 | 11.18 | 11.18 | 11.18 | 11.18 | 11.50 | 11.50 | 11.50 | 11.50 | 12.36 | 12.36 | 12.36 | 12.36 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 2.85 | 2.85 | 2.85 | 2.85 | 2.84 | 2.84 | 2.84 | 2.84 | 2.83 | 2.83 | 2.83 | 2.83 | 2.82 | 2.82 | 2.82 | 2.82 |
| 25 | TC | 10.06 | 10.06 | 10.17 | 10.29 | 10.69 | 10.69 | 10.69 | 10.69 | 11.01 | 11.01 | 11.01 | 11.01 | 11.84 | 11.84 | 11.84 | 11.84 |
| S/T | 0.75 | 0.85 | 0.95 | 1.00 | 0.59 | 0.69 | 0.78 | 0.88 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 |
| 30 | TC | 9.57 | 9.57 | 9.66 | 9.74 | 10.20 | 10.20 | 10.20 | 10.32 | 10.49 | 10.49 | 10.49 | 10.49 | 11.32 | 11.32 | 11.32 | 11.32 |
| S/T | 0.76 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 3.44 | 3.44 | 3.44 | 3.44 | 3.45 | 3.45 | 3.45 | 3.45 | 3.46 | 3.46 | 3.46 | 3.46 | 3.47 | 3.47 | 3.47 | 3.47 |
| 35 | TC | 9.11 | 9.20 | 9.28 | 9.37 | 9.68 | 9.68 | 9.68 | 9.77 | 10.00 | 10.00 | 10.14 | 10.00 | 10.78 | 10.78 | 10.78 | 10.78 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.72 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.76 | 3.76 | 3.76 | 3.76 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.79 | 3.78 | 3.81 | 3.81 | 3.81 | 3.81 |
| 40 | TC | 8.49 | 8.58 | 8.66 | 8.75 | 9.05 | 9.05 | 9.05 | 9.13 | 9.34 | 9.34 | 9.41 | 9.34 | 10.08 | 10.08 | 10.08 | 10.08 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 4.15 | 4.15 | 4.15 | 4.15 | 4.17 | 4.17 | 4.17 | 4.17 | 4.18 | 4.18 | 4.18 | 4.18 | 4.21 | 4.21 | 4.21 | 4.21 |
| 46 | TC | 7.86 | 7.94 | 8.03 | 8.11 | 8.40 | 8.40 | 8.40 | 8.48 | 8.65 | 8.65 | 8.65 | 8.65 | 9.37 | 9.37 | 9.37 | 9.37 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.74 | 0.86 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 4.62 | 4.62 | 4.62 | 4.62 | 4.64 | 4.64 | 4.64 | 4.64 | 4.65 | 4.65 | 4.65 | 4.65 | 4.69 | 4.69 | 4.69 | 4.69 |
| 50 | TC | 7.37 | 7.46 | 7.54 | 7.63 | 7.88 | 7.88 | 7.97 | 8.06 | 8.14 | 8.14 | 8.14 | 8.23 | 8.82 | 8.82 | 8.82 | 8.82 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.54 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.67 |
| PI | 5.00 | 5.00 | 5.00 | 5.00 | 5.02 | 5.02 | 5.02 | 5.02 | 5.03 | 5.03 | 5.03 | 5.03 | 5.07 | 5.07 | 5.07 | 5.07 |
| 1800 | -15 | TC | 11.28 | 11.40 | 11.52 | 11.64 | 11.87 | 11.87 | 11.87 | 11.99 | 12.15 | 12.15 | 12.15 | 12.15 | 12.92 | 12.92 | 12.92 | 12.92 |
| S/T | 0.75 | 0.86 | 0.98 | 1.00 | 0.59 | 0.69 | 0.79 | 0.89 | 0.51 | 0.61 | 0.70 | 0.81 | 0.33 | 0.42 | 0.52 | 0.61 |
| PI | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 |
| -10 | TC | 11.21 | 11.33 | 11.45 | 11.57 | 11.80 | 11.80 | 11.80 | 11.92 | 12.08 | 12.08 | 12.08 | 12.08 | 12.87 | 12.87 | 12.87 | 12.87 |
| S/T | 0.76 | 0.86 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.89 | 0.51 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.52 | 0.61 |
| PI | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 |
| -5 | TC | 11.14 | 11.26 | 11.38 | 11.50 | 11.76 | 11.76 | 11.76 | 11.88 | 12.04 | 12.04 | 12.04 | 12.04 | 12.84 | 12.84 | 12.84 | 12.84 |
| S/T | 0.76 | 0.87 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.90 | 0.52 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.53 | 0.61 |
| PI | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 |
| 0 | TC | 11.09 | 11.21 | 11.32 | 11.44 | 11.71 | 11.71 | 11.71 | 11.83 | 12.01 | 12.01 | 12.01 | 12.01 | 12.83 | 12.83 | 12.83 | 12.83 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.82 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 |
| 5 | TC | 11.03 | 11.15 | 11.27 | 11.38 | 11.67 | 11.67 | 11.67 | 11.79 | 11.97 | 11.97 | 11.97 | 11.97 | 12.82 | 12.82 | 12.82 | 12.82 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 |
| 10 | TC | 10.96 | 11.08 | 11.20 | 11.32 | 11.61 | 11.61 | 11.61 | 11.73 | 11.92 | 11.92 | 11.92 | 11.92 | 12.78 | 12.78 | 12.78 | 12.78 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.34 | 0.44 | 0.53 | 0.62 |
| PI | 2.75 | 2.75 | 2.75 | 2.75 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 |
| 15 | TC | 10.87 | 10.99 | 11.11 | 11.22 | 11.54 | 11.54 | 11.54 | 11.65 | 11.85 | 11.85 | 11.85 | 11.85 | 12.73 | 12.73 | 12.73 | 12.73 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 |
| 20 | TC | 10.75 | 10.87 | 10.98 | 11.10 | 11.41 | 11.41 | 11.41 | 11.53 | 11.73 | 11.73 | 11.73 | 11.73 | 12.62 | 12.62 | 12.62 | 12.62 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 2.91 | 2.91 | 2.91 | 2.91 | 2.90 | 2.90 | 2.90 | 2.90 | 2.89 | 2.89 | 2.89 | 2.89 | 2.88 | 2.88 | 2.88 | 2.88 |
| 25 | TC | 10.26 | 10.38 | 10.49 | 10.61 | 10.90 | 10.90 | 10.90 | 11.01 | 11.21 | 11.21 | 11.21 | 11.21 | 12.07 | 12.07 | 12.07 | 12.07 |
| S/T | 0.79 | 0.91 | 1.00 | 1.00 | 0.61 | 0.73 | 0.84 | 0.94 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 |
| 30 | TC | 9.77 | 9.86 | 9.95 | 10.03 | 10.41 | 10.41 | 10.41 | 10.52 | 10.72 | 10.72 | 10.72 | 10.72 | 11.53 | 11.53 | 11.53 | 11.53 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.97 | 0.54 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.53 | 3.53 | 3.53 | 3.53 | 3.54 | 3.54 | 3.54 | 3.54 |
| 35 | TC | 9.29 | 9.37 | 9.46 | 9.54 | 9.89 | 9.89 | 9.89 | 9.98 | 10.18 | 10.18 | 10.35 | 10.46 | 10.98 | 10.98 | 10.98 | 10.98 |
| S/T | 0.83 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.88 | 0.99 | 0.54 | 0.66 | 0.77 | 0.89 | 0.34 | 0.45 | 0.56 | 0.67 |
| PI | 3.84 | 3.84 | 3.84 | 3.84 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.87 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 |
| 40 | TC | 8.67 | 8.76 | 8.84 | 8.93 | 9.24 | 9.24 | 9.28 | 9.37 | 9.52 | 9.52 | 9.61 | 9.71 | 10.29 | 10.29 | 10.29 | 10.29 |
| S/T | 0.86 | 1.00 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.94 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 4.24 | 4.24 | 4.24 | 4.24 | 4.26 | 4.26 | 4.26 | 4.26 | 4.27 | 4.27 | 4.27 | 4.27 | 4.28 | 4.28 | 4.28 | 4.28 |
| 46 | TC | 8.03 | 8.12 | 8.20 | 8.29 | 8.58 | 8.58 | 8.66 | 8.75 | 8.83 | 8.83 | 8.83 | 8.92 | 9.57 | 9.57 | 9.57 | 9.57 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.83 | 0.96 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 4.71 | 4.71 | 4.71 | 4.71 | 4.74 | 4.74 | 4.74 | 4.74 | 4.75 | 4.75 | 4.75 | 4.75 | 4.79 | 4.79 | 4.79 | 4.79 |
| 50 | TC | 7.52 | 7.61 | 7.69 | 7.78 | 8.06 | 8.06 | 8.15 | 8.23 | 8.32 | 8.32 | 8.32 | 8.40 | 9.03 | 9.03 | 9.03 | 9.03 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.82 | 0.96 | 1.00 | 0.57 | 0.71 | 0.85 | 0.99 | 0.32 | 0.46 | 0.59 | 0.91 |
| PI | 5.10 | 5.10 | 5.10 | 5.10 | 5.13 | 5.13 | 5.13 | 5.13 | 5.14 | 5.14 | 5.14 | 5.14 | 5.18 | 5.18 | 5.18 | 5.18 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2100 | -15 | TC | 11.49 | 11.61 | 11.73 | 11.85 | 12.08 | 12.08 | 12.08 | 12.20 | 12.38 | 12.38 | 12.38 | 12.50 | 13.15 | 13.15 | 13.15 | 13.15 |
| S/T | 0.79 | 0.92 | 1.00 | 1.00 | 0.61 | 0.72 | 0.84 | 0.98 | 0.52 | 0.64 | 0.75 | 0.86 | 0.33 | 0.43 | 0.53 | 0.64 |
| PI | 2.74 | 2.74 | 2.74 | 2.74 | 2.73 | 2.73 | 2.73 | 2.73 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 |
| -10 | TC | 11.42 | 11.54 | 11.66 | 11.78 | 12.01 | 12.01 | 12.01 | 12.13 | 12.32 | 12.32 | 12.32 | 12.44 | 13.11 | 13.11 | 13.11 | 13.11 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.61 | 0.73 | 0.84 | 0.98 | 0.52 | 0.64 | 0.76 | 0.86 | 0.33 | 0.44 | 0.53 | 0.64 |
| PI | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.73 | 2.73 | 2.73 | 2.73 |
| -5 | TC | 11.35 | 11.47 | 11.59 | 11.71 | 11.97 | 11.97 | 11.97 | 12.08 | 12.28 | 12.28 | 12.28 | 12.39 | 13.07 | 13.07 | 13.07 | 13.07 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.61 | 0.73 | 0.85 | 0.99 | 0.53 | 0.64 | 0.76 | 0.87 | 0.33 | 0.44 | 0.54 | 0.64 |
| PI | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.73 | 2.73 | 2.73 | 2.73 |
| 0 | TC | 11.29 | 11.41 | 11.53 | 11.65 | 11.92 | 11.92 | 11.92 | 12.04 | 12.24 | 12.24 | 12.24 | 12.36 | 13.06 | 13.06 | 13.06 | 13.06 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.99 | 0.53 | 0.65 | 0.76 | 0.87 | 0.33 | 0.44 | 0.54 | 0.65 |
| PI | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.74 | 2.74 | 2.74 | 2.74 |
| 5 | TC | 11.24 | 11.36 | 11.47 | 11.59 | 11.87 | 11.87 | 11.87 | 11.99 | 12.20 | 12.20 | 12.20 | 12.32 | 13.05 | 13.05 | 13.05 | 13.05 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.33 | 0.44 | 0.54 | 0.65 |
| PI | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.75 | 2.75 | 2.75 | 2.75 | 2.76 | 2.76 | 2.76 | 2.76 |
| 10 | TC | 11.17 | 11.29 | 11.40 | 11.52 | 11.82 | 11.82 | 11.82 | 11.94 | 12.15 | 12.15 | 12.15 | 12.27 | 13.02 | 13.02 | 13.02 | 13.02 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.34 | 0.45 | 0.54 | 0.65 |
| PI | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.79 | 2.79 | 2.79 | 2.79 | 2.80 | 2.80 | 2.80 | 2.80 |
| 15 | TC | 11.08 | 11.19 | 11.31 | 11.43 | 11.74 | 11.74 | 11.74 | 11.86 | 12.08 | 12.08 | 12.08 | 12.19 | 12.96 | 12.96 | 12.96 | 12.96 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.55 | 0.66 |
| PI | 2.87 | 2.87 | 2.87 | 2.87 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.85 | 2.85 | 2.85 | 2.85 |
| 20 | TC | 10.95 | 11.07 | 11.18 | 11.30 | 11.61 | 11.61 | 11.61 | 11.73 | 11.96 | 11.96 | 11.96 | 12.07 | 12.85 | 12.85 | 12.85 | 12.85 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.55 | 0.66 |
| PI | 2.97 | 2.97 | 2.97 | 2.97 | 2.96 | 2.96 | 2.96 | 2.96 | 2.95 | 2.95 | 2.95 | 2.95 | 2.94 | 2.94 | 2.94 | 2.94 |
| 25 | TC | 10.46 | 10.58 | 10.69 | 10.81 | 11.10 | 11.10 | 11.21 | 11.33 | 11.44 | 11.44 | 11.44 | 11.56 | 12.30 | 12.30 | 12.30 | 12.30 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.77 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.68 |
| PI | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 |
| 30 | TC | 9.98 | 10.06 | 10.18 | 10.29 | 10.61 | 10.61 | 10.72 | 10.84 | 10.92 | 10.92 | 10.92 | 11.04 | 11.76 | 11.76 | 11.76 | 11.76 |
| S/T | 0.86 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.93 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 3.59 | 3.59 | 3.59 | 3.59 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.62 | 3.62 | 3.62 | 3.62 |
| 35 | TC | 9.46 | 9.54 | 9.63 | 9.72 | 10.06 | 10.06 | 10.18 | 10.29 | 10.38 | 10.38 | 10.55 | 10.67 | 11.21 | 11.21 | 11.21 | 11.21 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 3.92 | 3.92 | 3.92 | 3.92 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.95 | 3.94 | 3.97 | 3.97 | 3.97 | 3.97 |
| 40 | TC | 8.83 | 8.91 | 9.00 | 9.09 | 9.40 | 9.40 | 9.50 | 9.60 | 9.70 | 9.70 | 9.83 | 9.93 | 10.50 | 10.50 | 10.50 | 10.50 |
| S/T | 0.92 | 1.00 | 1.00 | 1.00 | 0.68 | 0.83 | 0.98 | 1.00 | 0.57 | 0.72 | 0.87 | 1.00 | 0.32 | 0.46 | 0.60 | 0.90 |
| PI | 4.32 | 4.32 | 4.32 | 4.32 | 4.34 | 4.34 | 4.34 | 4.34 | 4.35 | 4.35 | 4.36 | 4.35 | 4.39 | 4.39 | 4.39 | 4.39 |
| 46 | TC | 8.18 | 8.26 | 8.35 | 8.43 | 8.72 | 8.72 | 8.80 | 8.89 | 9.00 | 9.00 | 9.09 | 9.17 | 9.77 | 9.77 | 9.77 | 9.77 |
| S/T | 0.94 | 1.00 | 1.00 | 1.00 | 0.69 | 0.85 | 1.00 | 1.00 | 0.58 | 0.73 | 0.88 | 1.00 | 0.32 | 0.46 | 0.61 | 0.92 |
| PI | 4.81 | 4.81 | 4.81 | 4.81 | 4.83 | 4.83 | 4.83 | 4.83 | 4.85 | 4.85 | 4.85 | 4.85 | 4.89 | 4.89 | 4.89 | 4.89 |
| 50 | TC | 7.66 | 7.75 | 7.83 | 7.92 | 8.20 | 8.20 | 8.29 | 8.38 | 8.49 | 8.49 | 8.58 | 8.66 | 9.20 | 9.20 | 9.20 | 9.20 |
| S/T | 0.97 | 1.00 | 1.00 | 1.00 | 0.71 | 0.88 | 1.00 | 1.00 | 0.59 | 0.75 | 0.91 | 1.00 | 0.32 | 0.47 | 0.62 | 0.97 |
| PI | 5.21 | 5.21 | 5.21 | 5.21 | 5.23 | 5.23 | 5.23 | 5.23 | 5.25 | 5.25 | 5.25 | 5.25 | 5.29 | 5.29 | 5.29 | 5.29 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS036D8S+38QUS042D8S | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1500 | -15 | TC | 11.05 | 11.06 | 11.18 | 11.30 | 11.63 | 11.87 | 11.87 | 11.99 | 11.90 | 11.90 | 11.90 | 11.90 | 12.65 | 12.65 | 12.65 | 12.65 |
| S/T | 0.71 | 0.81 | 0.90 | 0.97 | 0.57 | 0.65 | 0.74 | 0.83 | 0.50 | 0.59 | 0.67 | 0.75 | 0.35 | 0.42 | 0.50 | 0.58 |
| PI | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 |
| -10 | TC | 10.99 | 11.00 | 11.11 | 11.23 | 11.56 | 11.80 | 11.80 | 11.92 | 11.84 | 11.84 | 11.84 | 11.84 | 12.60 | 12.60 | 12.60 | 12.60 |
| S/T | 0.72 | 0.82 | 0.90 | 0.97 | 0.57 | 0.66 | 0.75 | 0.83 | 0.50 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 |
| -5 | TC | 10.92 | 10.93 | 11.05 | 11.17 | 11.52 | 11.76 | 11.76 | 11.88 | 11.80 | 11.80 | 11.80 | 11.80 | 12.57 | 12.57 | 12.57 | 12.57 |
| S/T | 0.72 | 0.82 | 0.91 | 0.98 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.66 | 2.66 | 2.66 | 2.66 |
| 0 | TC | 10.87 | 10.87 | 10.99 | 11.11 | 11.47 | 11.71 | 11.71 | 11.83 | 11.77 | 11.77 | 11.77 | 11.77 | 12.56 | 12.56 | 12.56 | 12.56 |
| S/T | 0.73 | 0.82 | 0.91 | 0.98 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.60 | 0.68 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.67 | 2.67 | 2.67 | 2.67 |
| 5 | TC | 10.81 | 10.82 | 10.94 | 11.06 | 11.43 | 11.67 | 11.67 | 11.79 | 11.73 | 11.73 | 11.73 | 11.73 | 12.55 | 12.55 | 12.55 | 12.55 |
| S/T | 0.73 | 0.83 | 0.92 | 0.99 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.68 | 2.69 | 2.69 | 2.69 | 2.69 |
| 10 | TC | 10.75 | 10.75 | 10.87 | 10.99 | 11.38 | 11.61 | 11.61 | 11.73 | 11.68 | 11.68 | 11.68 | 11.68 | 12.52 | 12.52 | 12.52 | 12.52 |
| S/T | 0.73 | 0.83 | 0.92 | 0.99 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 2.73 | 2.73 | 2.73 | 2.73 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 |
| 15 | TC | 10.66 | 10.67 | 10.78 | 10.90 | 11.30 | 11.54 | 11.54 | 11.65 | 11.61 | 11.61 | 11.61 | 11.61 | 12.46 | 12.46 | 12.46 | 12.46 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.67 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 |
| 20 | TC | 10.54 | 10.55 | 10.66 | 10.78 | 11.18 | 11.18 | 11.18 | 11.18 | 11.50 | 11.50 | 11.50 | 11.50 | 12.36 | 12.36 | 12.36 | 12.36 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 2.89 | 2.89 | 2.89 | 2.89 | 2.88 | 2.88 | 2.88 | 2.88 | 2.87 | 2.87 | 2.87 | 2.87 | 2.86 | 2.86 | 2.86 | 2.86 |
| 25 | TC | 10.06 | 10.06 | 10.17 | 10.29 | 10.69 | 10.69 | 10.69 | 10.69 | 11.01 | 11.01 | 11.01 | 11.01 | 11.84 | 11.84 | 11.84 | 11.84 |
| S/T | 0.75 | 0.85 | 0.95 | 1.00 | 0.59 | 0.69 | 0.78 | 0.88 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 |
| 30 | TC | 9.57 | 9.57 | 9.66 | 9.74 | 10.20 | 10.20 | 10.20 | 10.32 | 10.49 | 10.49 | 10.49 | 10.49 | 11.32 | 11.32 | 11.32 | 11.32 |
| S/T | 0.76 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 3.49 | 3.49 | 3.49 | 3.49 | 3.50 | 3.50 | 3.50 | 3.50 | 3.50 | 3.50 | 3.50 | 3.50 | 3.52 | 3.52 | 3.52 | 3.52 |
| 35 | TC | 9.11 | 9.20 | 9.28 | 9.37 | 9.68 | 9.68 | 9.68 | 9.77 | 10.00 | 10.00 | 10.14 | 10.00 | 10.78 | 10.78 | 10.78 | 10.78 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.72 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.81 | 3.81 | 3.81 | 3.81 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.84 | 3.83 | 3.86 | 3.86 | 3.86 | 3.86 |
| 40 | TC | 8.49 | 8.58 | 8.66 | 8.75 | 9.05 | 9.05 | 9.05 | 9.13 | 9.34 | 9.34 | 9.41 | 9.34 | 10.08 | 10.08 | 10.08 | 10.08 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 4.21 | 4.21 | 4.21 | 4.21 | 4.23 | 4.23 | 4.23 | 4.23 | 4.23 | 4.23 | 4.24 | 4.23 | 4.26 | 4.26 | 4.26 | 4.26 |
| 46 | TC | 7.86 | 7.94 | 8.03 | 8.11 | 8.40 | 8.40 | 8.40 | 8.48 | 8.65 | 8.65 | 8.65 | 8.65 | 9.37 | 9.37 | 9.37 | 9.37 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.74 | 0.86 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 4.68 | 4.68 | 4.68 | 4.68 | 4.70 | 4.70 | 4.70 | 4.70 | 4.71 | 4.71 | 4.71 | 4.71 | 4.75 | 4.75 | 4.75 | 4.75 |
| 50 | TC | 7.37 | 7.46 | 7.54 | 7.63 | 7.88 | 7.88 | 7.97 | 8.06 | 8.14 | 8.14 | 8.14 | 8.23 | 8.82 | 8.82 | 8.82 | 8.82 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.54 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.67 |
| PI | 5.06 | 5.06 | 5.06 | 5.06 | 5.09 | 5.09 | 5.09 | 5.09 | 5.10 | 5.10 | 5.10 | 5.10 | 5.14 | 5.14 | 5.14 | 5.14 |
| 1800 | -15 | TC | 11.28 | 11.40 | 11.52 | 11.64 | 11.87 | 11.87 | 11.87 | 11.99 | 12.15 | 12.15 | 12.15 | 12.15 | 12.92 | 12.92 | 12.92 | 12.92 |
| S/T | 0.75 | 0.86 | 0.98 | 1.00 | 0.59 | 0.69 | 0.79 | 0.89 | 0.51 | 0.61 | 0.70 | 0.81 | 0.33 | 0.42 | 0.52 | 0.61 |
| PI | 2.72 | 2.72 | 2.72 | 2.72 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 |
| -10 | TC | 11.21 | 11.33 | 11.45 | 11.57 | 11.80 | 11.80 | 11.80 | 11.92 | 12.08 | 12.08 | 12.08 | 12.08 | 12.87 | 12.87 | 12.87 | 12.87 |
| S/T | 0.76 | 0.86 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.89 | 0.51 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.52 | 0.61 |
| PI | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.70 | 2.70 | 2.70 | 2.70 | 2.71 | 2.71 | 2.71 | 2.71 |
| -5 | TC | 11.14 | 11.26 | 11.38 | 11.50 | 11.76 | 11.76 | 11.76 | 11.88 | 12.04 | 12.04 | 12.04 | 12.04 | 12.84 | 12.84 | 12.84 | 12.84 |
| S/T | 0.76 | 0.87 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.90 | 0.52 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.53 | 0.61 |
| PI | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.70 | 2.71 | 2.71 | 2.71 | 2.71 |
| 0 | TC | 11.09 | 11.21 | 11.32 | 11.44 | 11.71 | 11.71 | 11.71 | 11.83 | 12.01 | 12.01 | 12.01 | 12.01 | 12.83 | 12.83 | 12.83 | 12.83 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.82 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.72 | 2.72 | 2.72 | 2.72 |
| 5 | TC | 11.03 | 11.15 | 11.27 | 11.38 | 11.67 | 11.67 | 11.67 | 11.79 | 11.97 | 11.97 | 11.97 | 11.97 | 12.82 | 12.82 | 12.82 | 12.82 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.33 | 0.43 | 0.53 | 0.62 |
| PI | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.73 | 2.73 | 2.73 | 2.73 | 2.74 | 2.74 | 2.74 | 2.74 |
| 10 | TC | 10.96 | 11.08 | 11.20 | 11.32 | 11.61 | 11.61 | 11.61 | 11.73 | 11.92 | 11.92 | 11.92 | 11.92 | 12.78 | 12.78 | 12.78 | 12.78 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.34 | 0.44 | 0.53 | 0.62 |
| PI | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.77 | 2.77 | 2.77 | 2.77 | 2.78 | 2.78 | 2.78 | 2.78 |
| 15 | TC | 10.87 | 10.99 | 11.11 | 11.22 | 11.54 | 11.54 | 11.54 | 11.65 | 11.85 | 11.85 | 11.85 | 11.85 | 12.73 | 12.73 | 12.73 | 12.73 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 2.85 | 2.85 | 2.85 | 2.85 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 |
| 20 | TC | 10.75 | 10.87 | 10.98 | 11.10 | 11.41 | 11.41 | 11.41 | 11.53 | 11.73 | 11.73 | 11.73 | 11.73 | 12.62 | 12.62 | 12.62 | 12.62 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.54 | 0.63 |
| PI | 2.95 | 2.95 | 2.95 | 2.95 | 2.94 | 2.94 | 2.94 | 2.94 | 2.93 | 2.93 | 2.93 | 2.93 | 2.92 | 2.92 | 2.92 | 2.92 |
| 25 | TC | 10.26 | 10.38 | 10.49 | 10.61 | 10.90 | 10.90 | 10.90 | 11.01 | 11.21 | 11.21 | 11.21 | 11.21 | 12.07 | 12.07 | 12.07 | 12.07 |
| S/T | 0.79 | 0.91 | 1.00 | 1.00 | 0.61 | 0.73 | 0.84 | 0.94 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 |
| 30 | TC | 9.77 | 9.86 | 9.95 | 10.03 | 10.41 | 10.41 | 10.41 | 10.52 | 10.72 | 10.72 | 10.72 | 10.72 | 11.53 | 11.53 | 11.53 | 11.53 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.97 | 0.54 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 3.56 | 3.56 | 3.56 | 3.56 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.59 | 3.59 | 3.59 | 3.59 |
| 35 | TC | 9.29 | 9.37 | 9.46 | 9.54 | 9.89 | 9.89 | 9.89 | 9.98 | 10.18 | 10.18 | 10.35 | 10.46 | 10.98 | 10.98 | 10.98 | 10.98 |
| S/T | 0.83 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.88 | 0.99 | 0.54 | 0.66 | 0.77 | 0.89 | 0.34 | 0.45 | 0.56 | 0.67 |
| PI | 3.89 | 3.89 | 3.89 | 3.89 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.92 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 |
| 40 | TC | 8.67 | 8.76 | 8.84 | 8.93 | 9.24 | 9.24 | 9.28 | 9.37 | 9.52 | 9.52 | 9.61 | 9.71 | 10.29 | 10.29 | 10.29 | 10.29 |
| S/T | 0.86 | 1.00 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.94 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 4.29 | 4.29 | 4.29 | 4.29 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.33 | 4.32 | 4.34 | 4.34 | 4.34 | 4.34 |
| 46 | TC | 8.03 | 8.12 | 8.20 | 8.29 | 8.58 | 8.58 | 8.66 | 8.75 | 8.83 | 8.83 | 8.83 | 8.92 | 9.57 | 9.57 | 9.57 | 9.57 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.83 | 0.96 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 4.77 | 4.77 | 4.77 | 4.77 | 4.80 | 4.80 | 4.80 | 4.80 | 4.81 | 4.81 | 4.81 | 4.81 | 4.85 | 4.85 | 4.85 | 4.85 |
| 50 | TC | 7.52 | 7.61 | 7.69 | 7.78 | 8.06 | 8.06 | 8.15 | 8.23 | 8.32 | 8.32 | 8.32 | 8.40 | 9.03 | 9.03 | 9.03 | 9.03 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.82 | 0.96 | 1.00 | 0.57 | 0.71 | 0.85 | 0.99 | 0.32 | 0.46 | 0.59 | 0.91 |
| PI | 5.17 | 5.17 | 5.17 | 5.17 | 5.19 | 5.19 | 5.19 | 5.19 | 5.21 | 5.21 | 5.21 | 5.21 | 5.25 | 5.25 | 5.25 | 5.25 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2100 | -15 | TC | 11.49 | 11.61 | 11.73 | 11.85 | 12.08 | 12.08 | 12.08 | 12.20 | 12.38 | 12.38 | 12.38 | 12.50 | 13.15 | 13.15 | 13.15 | 13.15 |
| S/T | 0.79 | 0.92 | 1.00 | 1.00 | 0.61 | 0.72 | 0.84 | 0.98 | 0.52 | 0.64 | 0.75 | 0.86 | 0.33 | 0.43 | 0.53 | 0.64 |
| PI | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |
| -10 | TC | 11.42 | 11.54 | 11.66 | 11.78 | 12.01 | 12.01 | 12.01 | 12.13 | 12.32 | 12.32 | 12.32 | 12.44 | 13.11 | 13.11 | 13.11 | 13.11 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.61 | 0.73 | 0.84 | 0.98 | 0.52 | 0.64 | 0.76 | 0.86 | 0.33 | 0.44 | 0.53 | 0.64 |
| PI | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |
| -5 | TC | 11.35 | 11.47 | 11.59 | 11.71 | 11.97 | 11.97 | 11.97 | 12.08 | 12.28 | 12.28 | 12.28 | 12.39 | 13.07 | 13.07 | 13.07 | 13.07 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.61 | 0.73 | 0.85 | 0.99 | 0.53 | 0.64 | 0.76 | 0.87 | 0.33 | 0.44 | 0.54 | 0.64 |
| PI | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.77 | 2.77 | 2.77 | 2.77 |
| 0 | TC | 11.29 | 11.41 | 11.53 | 11.65 | 11.92 | 11.92 | 11.92 | 12.04 | 12.24 | 12.24 | 12.24 | 12.36 | 13.06 | 13.06 | 13.06 | 13.06 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.99 | 0.53 | 0.65 | 0.76 | 0.87 | 0.33 | 0.44 | 0.54 | 0.65 |
| PI | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.78 | 2.78 | 2.78 | 2.78 |
| 5 | TC | 11.24 | 11.36 | 11.47 | 11.59 | 11.87 | 11.87 | 11.87 | 11.99 | 12.20 | 12.20 | 12.20 | 12.32 | 13.05 | 13.05 | 13.05 | 13.05 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.33 | 0.44 | 0.54 | 0.65 |
| PI | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.80 | 2.80 | 2.80 | 2.80 |
| 10 | TC | 11.17 | 11.29 | 11.40 | 11.52 | 11.82 | 11.82 | 11.82 | 11.94 | 12.15 | 12.15 | 12.15 | 12.27 | 13.02 | 13.02 | 13.02 | 13.02 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.34 | 0.45 | 0.54 | 0.65 |
| PI | 2.84 | 2.84 | 2.84 | 2.84 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 |
| 15 | TC | 11.08 | 11.19 | 11.31 | 11.43 | 11.74 | 11.74 | 11.74 | 11.86 | 12.08 | 12.08 | 12.08 | 12.19 | 12.96 | 12.96 | 12.96 | 12.96 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.55 | 0.66 |
| PI | 2.91 | 2.91 | 2.91 | 2.91 | 2.90 | 2.90 | 2.90 | 2.90 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 |
| 20 | TC | 10.95 | 11.07 | 11.18 | 11.30 | 11.61 | 11.61 | 11.61 | 11.73 | 11.96 | 11.96 | 11.96 | 12.07 | 12.85 | 12.85 | 12.85 | 12.85 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.55 | 0.66 |
| PI | 3.01 | 3.01 | 3.01 | 3.01 | 3.00 | 3.00 | 3.00 | 3.00 | 2.99 | 2.99 | 2.99 | 2.99 | 2.98 | 2.98 | 2.98 | 2.98 |
| 25 | TC | 10.46 | 10.58 | 10.69 | 10.81 | 11.10 | 11.10 | 11.21 | 11.33 | 11.44 | 11.44 | 11.44 | 11.56 | 12.30 | 12.30 | 12.30 | 12.30 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.77 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.68 |
| PI | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 |
| 30 | TC | 9.98 | 10.06 | 10.18 | 10.29 | 10.61 | 10.61 | 10.72 | 10.84 | 10.92 | 10.92 | 10.92 | 11.04 | 11.76 | 11.76 | 11.76 | 11.76 |
| S/T | 0.86 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.93 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 3.63 | 3.63 | 3.63 | 3.63 | 3.64 | 3.64 | 3.64 | 3.64 | 3.65 | 3.65 | 3.65 | 3.65 | 3.66 | 3.66 | 3.66 | 3.66 |
| 35 | TC | 9.46 | 9.54 | 9.63 | 9.72 | 10.06 | 10.06 | 10.18 | 10.29 | 10.38 | 10.38 | 10.55 | 10.67 | 11.21 | 11.21 | 11.21 | 11.21 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 3.97 | 3.97 | 3.97 | 3.97 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 4.00 | 3.99 | 4.02 | 4.02 | 4.02 | 4.02 |
| 40 | TC | 8.83 | 8.91 | 9.00 | 9.09 | 9.40 | 9.40 | 9.50 | 9.60 | 9.70 | 9.70 | 9.83 | 9.93 | 10.50 | 10.50 | 10.50 | 10.50 |
| S/T | 0.92 | 1.00 | 1.00 | 1.00 | 0.68 | 0.83 | 0.98 | 1.00 | 0.57 | 0.72 | 0.87 | 1.00 | 0.32 | 0.46 | 0.60 | 0.90 |
| PI | 4.38 | 4.38 | 4.38 | 4.38 | 4.40 | 4.40 | 4.40 | 4.40 | 4.41 | 4.41 | 4.41 | 4.41 | 4.44 | 4.44 | 4.44 | 4.44 |
| 46 | TC | 8.18 | 8.26 | 8.35 | 8.43 | 8.72 | 8.72 | 8.80 | 8.89 | 9.00 | 9.00 | 9.09 | 9.17 | 9.77 | 9.77 | 9.77 | 9.77 |
| S/T | 0.94 | 1.00 | 1.00 | 1.00 | 0.69 | 0.85 | 1.00 | 1.00 | 0.58 | 0.73 | 0.88 | 1.00 | 0.32 | 0.46 | 0.61 | 0.92 |
| PI | 4.87 | 4.87 | 4.87 | 4.87 | 4.89 | 4.89 | 4.89 | 4.89 | 4.91 | 4.91 | 4.91 | 4.91 | 4.95 | 4.95 | 4.95 | 4.95 |
| 50 | TC | 7.66 | 7.75 | 7.83 | 7.92 | 8.20 | 8.20 | 8.29 | 8.38 | 8.49 | 8.49 | 8.58 | 8.66 | 9.20 | 9.20 | 9.20 | 9.20 |
| S/T | 0.97 | 1.00 | 1.00 | 1.00 | 0.71 | 0.88 | 1.00 | 1.00 | 0.59 | 0.75 | 0.91 | 1.00 | 0.32 | 0.47 | 0.62 | 0.97 |
| PI | 5.27 | 5.27 | 5.27 | 5.27 | 5.30 | 5.30 | 5.30 | 5.30 | 5.31 | 5.31 | 5.31 | 5.31 | 5.35 | 5.35 | 5.35 | 5.35 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS042D8S+38QUS036D8T | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1680 | -15 | TC | 12.59 | 12.60 | 12.72 | 12.84 | 13.24 | 13.51 | 13.51 | 13.66 | 13.57 | 13.57 | 13.57 | 13.57 | 14.41 | 14.41 | 14.41 | 14.41 |
| S/T | 0.71 | 0.80 | 0.89 | 0.97 | 0.57 | 0.65 | 0.73 | 0.82 | 0.50 | 0.58 | 0.67 | 0.75 | 0.35 | 0.42 | 0.50 | 0.58 |
| PI | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 |
| -10 | TC | 12.51 | 12.52 | 12.64 | 12.76 | 13.16 | 13.44 | 13.44 | 13.59 | 13.50 | 13.50 | 13.50 | 13.50 | 14.36 | 14.36 | 14.36 | 14.36 |
| S/T | 0.72 | 0.81 | 0.89 | 0.97 | 0.57 | 0.66 | 0.74 | 0.82 | 0.50 | 0.58 | 0.67 | 0.76 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.78 | 2.78 | 2.78 | 2.78 | 2.79 | 2.79 | 2.79 | 2.79 |
| -5 | TC | 12.44 | 12.45 | 12.57 | 12.69 | 13.11 | 13.39 | 13.39 | 13.53 | 13.45 | 13.45 | 13.45 | 13.45 | 14.32 | 14.32 | 14.32 | 14.32 |
| S/T | 0.72 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.74 | 0.83 | 0.51 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.79 | 2.78 | 2.78 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79 | 2.78 | 2.78 | 2.78 | 2.78 | 2.80 | 2.80 | 2.80 | 2.80 |
| 0 | TC | 12.38 | 12.39 | 12.50 | 12.62 | 13.06 | 13.34 | 13.34 | 13.48 | 13.41 | 13.41 | 13.41 | 13.41 | 14.31 | 14.31 | 14.31 | 14.31 |
| S/T | 0.73 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.74 | 0.83 | 0.51 | 0.59 | 0.68 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.80 | 2.81 | 2.81 | 2.81 | 2.81 |
| 5 | TC | 12.31 | 12.32 | 12.44 | 12.56 | 13.02 | 13.28 | 13.28 | 13.43 | 13.37 | 13.37 | 13.37 | 13.37 | 14.30 | 14.30 | 14.30 | 14.30 |
| S/T | 0.73 | 0.82 | 0.91 | 0.99 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.68 | 0.77 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.83 | 2.83 | 2.83 | 2.83 |
| 10 | TC | 12.24 | 12.25 | 12.37 | 12.48 | 12.95 | 13.22 | 13.22 | 13.37 | 13.31 | 13.31 | 13.31 | 13.31 | 14.26 | 14.26 | 14.26 | 14.26 |
| S/T | 0.73 | 0.82 | 0.91 | 0.99 | 0.58 | 0.67 | 0.75 | 0.84 | 0.51 | 0.59 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 2.87 | 2.87 | 2.87 | 2.87 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 |
| 15 | TC | 12.14 | 12.15 | 12.27 | 12.38 | 12.87 | 13.13 | 13.13 | 13.28 | 13.23 | 13.23 | 13.23 | 13.23 | 14.20 | 14.20 | 14.20 | 14.20 |
| S/T | 0.74 | 0.83 | 0.92 | 1.00 | 0.59 | 0.67 | 0.76 | 0.85 | 0.52 | 0.60 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 2.94 | 2.94 | 2.94 | 2.94 | 2.93 | 2.93 | 2.93 | 2.93 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 |
| 20 | TC | 12.00 | 12.01 | 12.13 | 12.24 | 12.73 | 12.73 | 12.73 | 12.73 | 13.10 | 13.10 | 13.10 | 13.10 | 14.08 | 14.08 | 14.08 | 14.08 |
| S/T | 0.74 | 0.83 | 0.92 | 1.00 | 0.59 | 0.68 | 0.76 | 0.85 | 0.52 | 0.60 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 3.04 | 3.04 | 3.04 | 3.04 | 3.03 | 3.03 | 3.03 | 3.03 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.01 | 3.01 | 3.01 |
| 25 | TC | 11.44 | 11.44 | 11.55 | 11.67 | 12.16 | 12.16 | 12.16 | 12.16 | 12.53 | 12.53 | 12.53 | 12.53 | 13.48 | 13.48 | 13.48 | 13.48 |
| S/T | 0.75 | 0.85 | 0.94 | 1.00 | 0.59 | 0.68 | 0.78 | 0.87 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.60 |
| PI | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 |
| 30 | TC | 10.92 | 10.92 | 11.03 | 11.15 | 11.61 | 11.61 | 11.61 | 11.72 | 11.95 | 11.95 | 11.95 | 11.95 | 12.87 | 12.87 | 12.87 | 12.87 |
| S/T | 0.76 | 0.86 | 0.96 | 1.00 | 0.60 | 0.69 | 0.79 | 0.88 | 0.52 | 0.62 | 0.71 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 3.67 | 3.67 | 3.67 | 3.67 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.70 | 3.70 | 3.70 | 3.70 |
| 35 | TC | 10.37 | 10.37 | 10.49 | 10.60 | 11.03 | 11.03 | 11.03 | 11.15 | 11.38 | 11.38 | 11.55 | 11.38 | 12.27 | 12.27 | 12.27 | 12.27 |
| S/T | 0.77 | 0.88 | 0.98 | 1.00 | 0.60 | 0.71 | 0.81 | 0.91 | 0.53 | 0.62 | 0.72 | 0.82 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 4.01 | 4.01 | 4.01 | 4.01 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.04 | 4.03 | 4.06 | 4.06 | 4.06 | 4.06 |
| 40 | TC | 9.68 | 9.71 | 9.82 | 9.92 | 10.32 | 10.32 | 10.32 | 10.42 | 10.65 | 10.65 | 10.74 | 10.65 | 11.49 | 11.49 | 11.49 | 11.49 |
| S/T | 0.80 | 0.91 | 1.00 | 1.00 | 0.62 | 0.73 | 0.84 | 0.95 | 0.53 | 0.64 | 0.75 | 0.86 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 4.43 | 4.43 | 4.43 | 4.43 | 4.44 | 4.44 | 4.44 | 4.44 | 4.45 | 4.45 | 4.46 | 4.45 | 4.49 | 4.49 | 4.49 | 4.49 |
| 46 | TC | 8.95 | 9.03 | 9.12 | 9.20 | 9.57 | 9.57 | 9.57 | 9.66 | 9.89 | 9.89 | 9.89 | 9.89 | 10.68 | 10.68 | 10.68 | 10.68 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 0.97 | 0.54 | 0.65 | 0.76 | 0.88 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 4.92 | 4.92 | 4.92 | 4.92 | 4.94 | 4.94 | 4.94 | 4.94 | 4.96 | 4.96 | 4.96 | 4.96 | 5.00 | 5.00 | 5.00 | 5.00 |
| 50 | TC | 8.40 | 8.49 | 8.57 | 8.66 | 8.97 | 8.97 | 8.97 | 9.06 | 9.29 | 9.29 | 9.29 | 9.37 | 10.06 | 10.06 | 10.06 | 10.06 |
| S/T | 0.83 | 0.96 | 1.00 | 1.00 | 0.63 | 0.76 | 0.88 | 1.00 | 0.54 | 0.66 | 0.78 | 0.90 | 0.33 | 0.45 | 0.56 | 0.67 |
| PI | 5.33 | 5.33 | 5.33 | 5.33 | 5.35 | 5.35 | 5.35 | 5.35 | 5.36 | 5.36 | 5.36 | 5.36 | 5.41 | 5.41 | 5.41 | 5.41 |
| 2040 | -15 | TC | 12.84 | 12.96 | 13.08 | 13.20 | 13.51 | 13.51 | 13.51 | 13.66 | 13.84 | 13.84 | 13.84 | 13.84 | 14.71 | 14.71 | 14.71 | 14.71 |
| S/T | 0.75 | 0.86 | 0.98 | 1.00 | 0.59 | 0.69 | 0.79 | 0.89 | 0.51 | 0.61 | 0.70 | 0.81 | 0.33 | 0.42 | 0.51 | 0.61 |
| PI | 2.86 | 2.86 | 2.86 | 2.86 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.84 | 2.84 | 2.84 | 2.84 |
| -10 | TC | 12.77 | 12.89 | 13.01 | 13.13 | 13.44 | 13.44 | 13.44 | 13.59 | 13.77 | 13.77 | 13.77 | 13.77 | 14.66 | 14.66 | 14.66 | 14.66 |
| S/T | 0.76 | 0.86 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.89 | 0.51 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.51 | 0.61 |
| PI | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.85 | 2.85 | 2.85 | 2.85 |
| -5 | TC | 12.69 | 12.81 | 12.93 | 13.05 | 13.39 | 13.39 | 13.39 | 13.53 | 13.72 | 13.72 | 13.72 | 13.72 | 14.62 | 14.62 | 14.62 | 14.62 |
| S/T | 0.76 | 0.87 | 0.99 | 1.00 | 0.59 | 0.69 | 0.80 | 0.90 | 0.52 | 0.61 | 0.71 | 0.82 | 0.33 | 0.43 | 0.52 | 0.61 |
| PI | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.85 | 2.85 | 2.85 | 2.85 |
| 0 | TC | 12.63 | 12.75 | 12.86 | 12.98 | 13.34 | 13.34 | 13.34 | 13.48 | 13.68 | 13.68 | 13.68 | 13.68 | 14.61 | 14.61 | 14.61 | 14.61 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.82 | 0.33 | 0.43 | 0.52 | 0.62 |
| PI | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.86 | 2.86 | 2.86 | 2.86 |
| 5 | TC | 12.56 | 12.68 | 12.80 | 12.92 | 13.28 | 13.28 | 13.28 | 13.43 | 13.64 | 13.64 | 13.64 | 13.64 | 14.60 | 14.60 | 14.60 | 14.60 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.33 | 0.43 | 0.52 | 0.62 |
| PI | 2.88 | 2.88 | 2.88 | 2.88 | 2.88 | 2.88 | 2.88 | 2.88 | 2.87 | 2.87 | 2.87 | 2.87 | 2.88 | 2.88 | 2.88 | 2.88 |
| 10 | TC | 12.49 | 12.60 | 12.72 | 12.84 | 13.22 | 13.22 | 13.22 | 13.37 | 13.58 | 13.58 | 13.58 | 13.58 | 14.56 | 14.56 | 14.56 | 14.56 |
| S/T | 0.77 | 0.88 | 1.00 | 1.00 | 0.60 | 0.70 | 0.81 | 0.91 | 0.52 | 0.62 | 0.72 | 0.83 | 0.34 | 0.44 | 0.52 | 0.62 |
| PI | 2.93 | 2.93 | 2.93 | 2.93 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 |
| 15 | TC | 12.39 | 12.50 | 12.62 | 12.73 | 13.13 | 13.13 | 13.13 | 13.28 | 13.50 | 13.50 | 13.50 | 13.50 | 14.50 | 14.50 | 14.50 | 14.50 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 3.00 | 3.00 | 3.00 | 3.00 | 2.99 | 2.99 | 2.99 | 2.99 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 |
| 20 | TC | 12.25 | 12.36 | 12.48 | 12.59 | 12.99 | 12.99 | 12.99 | 13.14 | 13.37 | 13.37 | 13.37 | 13.37 | 14.37 | 14.37 | 14.37 | 14.37 |
| S/T | 0.78 | 0.89 | 0.99 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 3.10 | 3.10 | 3.10 | 3.10 | 3.09 | 3.09 | 3.09 | 3.09 | 3.08 | 3.08 | 3.08 | 3.08 | 3.07 | 3.07 | 3.07 | 3.07 |
| 25 | TC | 11.67 | 11.79 | 11.90 | 12.02 | 12.42 | 12.42 | 12.42 | 12.53 | 12.79 | 12.79 | 12.79 | 12.79 | 13.74 | 13.74 | 13.74 | 13.74 |
| S/T | 0.79 | 0.91 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.94 | 0.53 | 0.64 | 0.75 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 |
| 30 | TC | 11.13 | 11.24 | 11.36 | 11.47 | 11.84 | 11.84 | 11.84 | 11.96 | 12.19 | 12.19 | 12.19 | 12.19 | 13.14 | 13.14 | 13.14 | 13.14 |
| S/T | 0.81 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.96 | 0.54 | 0.65 | 0.76 | 0.87 | 0.34 | 0.44 | 0.55 | 0.65 |
| PI | 3.74 | 3.74 | 3.74 | 3.74 | 3.75 | 3.75 | 3.75 | 3.75 | 3.76 | 3.76 | 3.76 | 3.76 | 3.77 | 3.77 | 3.77 | 3.77 |
| 35 | TC | 10.58 | 10.69 | 10.81 | 10.92 | 11.27 | 11.27 | 11.27 | 11.38 | 11.61 | 11.61 | 11.79 | 11.90 | 12.53 | 12.53 | 12.53 | 12.53 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 4.09 | 4.09 | 4.09 | 4.09 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.12 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 |
| 40 | TC | 9.86 | 9.96 | 10.06 | 10.16 | 10.50 | 10.50 | 10.54 | 10.64 | 10.83 | 10.83 | 10.92 | 11.03 | 11.71 | 11.71 | 11.71 | 11.71 |
| S/T | 0.86 | 1.00 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.93 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 4.52 | 4.52 | 4.52 | 4.52 | 4.54 | 4.54 | 4.54 | 4.54 | 4.55 | 4.55 | 4.56 | 4.55 | 4.57 | 4.57 | 4.57 | 4.57 |
| 46 | TC | 9.13 | 9.21 | 9.30 | 9.38 | 9.72 | 9.72 | 9.81 | 9.89 | 10.04 | 10.04 | 10.04 | 10.15 | 10.89 | 10.89 | 10.89 | 10.89 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.83 | 0.96 | 0.33 | 0.45 | 0.58 | 0.70 |
| PI | 5.03 | 5.03 | 5.03 | 5.03 | 5.05 | 5.05 | 5.05 | 5.05 | 5.07 | 5.07 | 5.07 | 5.07 | 5.11 | 5.11 | 5.11 | 5.11 |
| 50 | TC | 8.56 | 8.64 | 8.73 | 8.81 | 9.16 | 9.16 | 9.24 | 9.33 | 9.44 | 9.44 | 9.44 | 9.52 | 10.24 | 10.24 | 10.24 | 10.24 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.82 | 0.96 | 1.00 | 0.56 | 0.71 | 0.85 | 0.99 | 0.32 | 0.46 | 0.59 | 0.91 |
| PI | 5.45 | 5.45 | 5.45 | 5.45 | 5.47 | 5.47 | 5.47 | 5.47 | 5.48 | 5.48 | 5.48 | 5.48 | 5.53 | 5.53 | 5.53 | 5.53 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2400 | -15 | TC | 13.08 | 13.20 | 13.33 | 13.45 | 13.78 | 13.78 | 13.78 | 13.93 | 14.11 | 14.11 | 14.11 | 14.26 | 14.97 | 14.97 | 14.97 | 14.97 |
| S/T | 0.79 | 0.92 | 1.00 | 1.00 | 0.61 | 0.72 | 0.84 | 0.98 | 0.52 | 0.64 | 0.75 | 0.86 | 0.33 | 0.43 | 0.54 | 0.65 |
| PI | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 |
| -10 | TC | 13.01 | 13.13 | 13.25 | 13.37 | 13.70 | 13.70 | 13.70 | 13.85 | 14.04 | 14.04 | 14.04 | 14.19 | 14.92 | 14.92 | 14.92 | 14.92 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.61 | 0.73 | 0.84 | 0.98 | 0.52 | 0.64 | 0.76 | 0.86 | 0.33 | 0.44 | 0.54 | 0.65 |
| PI | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.90 | 2.89 | 2.89 | 2.89 | 2.89 | 2.90 | 2.90 | 2.90 | 2.90 |
| -5 | TC | 12.93 | 13.05 | 13.17 | 13.29 | 13.65 | 13.65 | 13.65 | 13.80 | 13.99 | 13.99 | 13.99 | 14.13 | 14.89 | 14.89 | 14.89 | 14.89 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.61 | 0.73 | 0.85 | 0.99 | 0.53 | 0.64 | 0.76 | 0.87 | 0.33 | 0.44 | 0.55 | 0.65 |
| PI | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.91 | 2.91 | 2.91 | 2.91 |
| 0 | TC | 12.86 | 12.98 | 13.10 | 13.22 | 13.60 | 13.60 | 13.60 | 13.75 | 13.95 | 13.95 | 13.95 | 14.10 | 14.87 | 14.87 | 14.87 | 14.87 |
| S/T | 0.80 | 0.93 | 1.00 | 1.00 | 0.62 | 0.74 | 0.85 | 0.99 | 0.53 | 0.65 | 0.76 | 0.87 | 0.33 | 0.44 | 0.55 | 0.66 |
| PI | 2.90 | 2.90 | 2.90 | 2.90 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.92 | 2.92 | 2.92 | 2.92 |
| 5 | TC | 12.80 | 12.92 | 13.04 | 13.15 | 13.55 | 13.55 | 13.55 | 13.70 | 13.90 | 13.90 | 13.90 | 14.05 | 14.86 | 14.86 | 14.86 | 14.86 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.33 | 0.44 | 0.55 | 0.66 |
| PI | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.94 | 2.94 | 2.94 | 2.94 |
| 10 | TC | 12.72 | 12.84 | 12.96 | 13.07 | 13.48 | 13.48 | 13.48 | 13.63 | 13.85 | 13.85 | 13.85 | 13.99 | 14.82 | 14.82 | 14.82 | 14.82 |
| S/T | 0.81 | 0.94 | 1.00 | 1.00 | 0.62 | 0.74 | 0.86 | 1.00 | 0.53 | 0.65 | 0.77 | 0.88 | 0.34 | 0.45 | 0.55 | 0.66 |
| PI | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.97 | 2.97 | 2.97 | 2.97 | 2.98 | 2.98 | 2.98 | 2.98 |
| 15 | TC | 12.62 | 12.73 | 12.85 | 12.97 | 13.39 | 13.39 | 13.39 | 13.54 | 13.76 | 13.76 | 13.76 | 13.91 | 14.76 | 14.76 | 14.76 | 14.76 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.56 | 0.67 |
| PI | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 |
| 20 | TC | 12.48 | 12.59 | 12.71 | 12.82 | 13.25 | 13.25 | 13.25 | 13.40 | 13.63 | 13.63 | 13.63 | 13.77 | 14.63 | 14.63 | 14.63 | 14.63 |
| S/T | 0.82 | 0.95 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.99 | 0.54 | 0.66 | 0.78 | 0.89 | 0.34 | 0.45 | 0.56 | 0.67 |
| PI | 3.16 | 3.16 | 3.16 | 3.16 | 3.15 | 3.15 | 3.15 | 3.15 | 3.14 | 3.14 | 3.14 | 3.14 | 3.13 | 3.13 | 3.13 | 3.13 |
| 25 | TC | 11.90 | 12.02 | 12.13 | 12.25 | 12.65 | 12.65 | 12.76 | 12.88 | 13.02 | 13.02 | 13.02 | 13.17 | 14.03 | 14.03 | 14.03 | 14.03 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.77 | 0.89 | 1.00 | 0.55 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.68 |
| PI | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 |
| 30 | TC | 11.36 | 11.47 | 11.59 | 11.70 | 12.07 | 12.07 | 12.19 | 12.30 | 12.45 | 12.45 | 12.45 | 12.56 | 13.40 | 13.40 | 13.40 | 13.40 |
| S/T | 0.86 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.91 | 1.00 | 0.55 | 0.68 | 0.81 | 0.94 | 0.33 | 0.45 | 0.57 | 0.69 |
| PI | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.83 | 3.83 | 3.83 | 3.83 | 3.85 | 3.85 | 3.85 | 3.85 |
| 35 | TC | 10.78 | 10.90 | 11.01 | 11.13 | 11.47 | 11.47 | 11.59 | 11.70 | 11.84 | 11.84 | 12.02 | 12.13 | 12.76 | 12.76 | 12.76 | 12.76 |
| S/T | 0.88 | 1.00 | 1.00 | 1.00 | 0.66 | 0.80 | 0.93 | 1.00 | 0.56 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.58 | 0.71 |
| PI | 4.17 | 4.17 | 4.17 | 4.17 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.20 | 4.19 | 4.22 | 4.22 | 4.22 | 4.22 |
| 40 | TC | 10.04 | 10.14 | 10.24 | 10.34 | 10.70 | 10.70 | 10.80 | 10.91 | 11.04 | 11.04 | 11.19 | 11.30 | 11.93 | 11.93 | 11.93 | 11.93 |
| S/T | 0.92 | 1.00 | 1.00 | 1.00 | 0.68 | 0.83 | 0.98 | 1.00 | 0.57 | 0.72 | 0.87 | 1.00 | 0.32 | 0.46 | 0.60 | 0.90 |
| PI | 4.61 | 4.61 | 4.61 | 4.61 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.64 | 4.63 | 4.67 | 4.67 | 4.67 | 4.67 |
| 46 | TC | 9.30 | 9.38 | 9.47 | 9.55 | 9.92 | 9.92 | 10.01 | 10.12 | 10.24 | 10.24 | 10.35 | 10.46 | 11.09 | 11.09 | 11.09 | 11.09 |
| S/T | 0.94 | 1.00 | 1.00 | 1.00 | 0.69 | 0.85 | 1.00 | 1.00 | 0.58 | 0.73 | 0.88 | 1.00 | 0.32 | 0.46 | 0.61 | 0.92 |
| PI | 5.13 | 5.13 | 5.13 | 5.13 | 5.15 | 5.15 | 5.15 | 5.15 | 5.16 | 5.16 | 5.16 | 5.16 | 5.21 | 5.21 | 5.21 | 5.21 |
| 50 | TC | 8.73 | 8.81 | 8.90 | 8.98 | 9.33 | 9.33 | 9.41 | 9.50 | 9.64 | 9.64 | 9.72 | 9.81 | 10.46 | 10.46 | 10.46 | 10.46 |
| S/T | 0.97 | 1.00 | 1.00 | 1.00 | 0.71 | 0.88 | 1.00 | 1.00 | 0.59 | 0.75 | 0.91 | 1.00 | 0.32 | 0.47 | 0.62 | 0.97 |
| PI | 5.55 | 5.55 | 5.55 | 5.55 | 5.57 | 5.57 | 5.57 | 5.57 | 5.59 | 5.59 | 5.59 | 5.59 | 5.63 | 5.63 | 5.63 | 5.63 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS048D8S+38QUS048D8T | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1680 | -15 | TC | 14.70 | 14.69 | 14.69 | 14.84 | 15.46 | 15.79 | 15.79 | 15.79 | 15.84 | 15.84 | 15.84 | 15.84 | 16.83 | 16.83 | 16.83 | 16.83 |
| S/T | 0.69 | 0.76 | 0.84 | 0.92 | 0.55 | 0.63 | 0.70 | 0.77 | 0.49 | 0.57 | 0.64 | 0.70 | 0.36 | 0.42 | 0.49 | 0.55 |
| PI | 3.19 | 3.19 | 3.19 | 3.19 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.17 | 3.17 | 3.17 | 3.17 |
| -10 | TC | 14.61 | 14.60 | 14.60 | 14.75 | 15.37 | 15.71 | 15.71 | 15.71 | 15.76 | 15.76 | 15.76 | 15.76 | 16.77 | 16.77 | 16.77 | 16.77 |
| S/T | 0.69 | 0.77 | 0.84 | 0.92 | 0.55 | 0.63 | 0.71 | 0.78 | 0.49 | 0.57 | 0.64 | 0.71 | 0.36 | 0.43 | 0.49 | 0.55 |
| PI | 3.18 | 3.18 | 3.18 | 3.18 | 3.17 | 3.17 | 3.17 | 3.17 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 |
| -5 | TC | 14.52 | 14.51 | 14.51 | 14.66 | 15.31 | 15.65 | 15.65 | 15.65 | 15.70 | 15.70 | 15.70 | 15.70 | 16.73 | 16.73 | 16.73 | 16.73 |
| S/T | 0.69 | 0.77 | 0.85 | 0.93 | 0.56 | 0.63 | 0.71 | 0.78 | 0.50 | 0.58 | 0.64 | 0.71 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 |
| 0 | TC | 14.45 | 14.44 | 14.44 | 14.59 | 15.26 | 15.59 | 15.59 | 15.59 | 15.66 | 15.66 | 15.66 | 15.66 | 16.71 | 16.71 | 16.71 | 16.71 |
| S/T | 0.70 | 0.77 | 0.85 | 0.93 | 0.56 | 0.64 | 0.72 | 0.78 | 0.50 | 0.58 | 0.65 | 0.72 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.18 | 3.19 | 3.19 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 |
| 5 | TC | 14.38 | 14.37 | 14.37 | 14.51 | 15.20 | 15.53 | 15.53 | 15.53 | 15.61 | 15.61 | 15.61 | 15.61 | 16.70 | 16.70 | 16.70 | 16.70 |
| S/T | 0.70 | 0.78 | 0.86 | 0.94 | 0.56 | 0.64 | 0.72 | 0.79 | 0.50 | 0.58 | 0.65 | 0.72 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.21 | 3.22 | 3.22 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.22 | 3.22 | 3.22 | 3.22 |
| 10 | TC | 14.29 | 14.28 | 14.28 | 14.43 | 15.13 | 15.45 | 15.45 | 15.45 | 15.54 | 15.54 | 15.54 | 15.54 | 16.66 | 16.66 | 16.66 | 16.66 |
| S/T | 0.70 | 0.78 | 0.86 | 0.94 | 0.56 | 0.64 | 0.72 | 0.79 | 0.50 | 0.58 | 0.65 | 0.72 | 0.37 | 0.44 | 0.50 | 0.56 |
| PI | 3.27 | 3.27 | 3.27 | 3.27 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 |
| 15 | TC | 14.18 | 14.16 | 14.16 | 14.31 | 15.02 | 15.35 | 15.35 | 15.35 | 15.45 | 15.45 | 15.45 | 15.45 | 16.59 | 16.59 | 16.59 | 16.59 |
| S/T | 0.71 | 0.79 | 0.87 | 0.95 | 0.57 | 0.65 | 0.73 | 0.80 | 0.51 | 0.59 | 0.66 | 0.73 | 0.37 | 0.44 | 0.51 | 0.57 |
| PI | 3.35 | 3.35 | 3.35 | 3.35 | 3.33 | 3.33 | 3.33 | 3.33 | 3.34 | 3.34 | 3.34 | 3.34 | 3.33 | 3.33 | 3.33 | 3.33 |
| 20 | TC | 14.02 | 14.00 | 14.00 | 14.15 | 14.87 | 14.87 | 14.87 | 14.87 | 15.30 | 15.30 | 15.30 | 15.30 | 16.44 | 16.44 | 16.44 | 16.44 |
| S/T | 0.71 | 0.79 | 0.87 | 0.95 | 0.57 | 0.65 | 0.73 | 0.80 | 0.51 | 0.59 | 0.66 | 0.73 | 0.37 | 0.44 | 0.51 | 0.57 |
| PI | 3.46 | 3.47 | 3.47 | 3.46 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.43 | 3.43 | 3.43 | 3.43 |
| 25 | TC | 13.37 | 13.37 | 13.37 | 13.52 | 14.21 | 14.21 | 14.21 | 14.21 | 14.64 | 14.64 | 14.64 | 14.64 | 15.73 | 15.73 | 15.73 | 15.73 |
| S/T | 0.72 | 0.80 | 0.88 | 0.96 | 0.58 | 0.66 | 0.74 | 0.82 | 0.51 | 0.59 | 0.67 | 0.74 | 0.37 | 0.44 | 0.51 | 0.58 |
| PI | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.81 | 3.81 | 3.81 | 3.81 | 3.82 | 3.82 | 3.82 | 3.82 |
| 30 | TC | 12.74 | 12.74 | 12.86 | 12.97 | 13.55 | 13.55 | 13.55 | 13.55 | 13.95 | 13.95 | 13.95 | 13.95 | 15.04 | 15.04 | 15.04 | 15.04 |
| S/T | 0.72 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.75 | 0.83 | 0.51 | 0.60 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 4.18 | 4.18 | 4.18 | 4.18 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.21 | 4.21 | 4.21 | 4.21 |
| 35 | TC | 12.11 | 12.11 | 12.23 | 12.34 | 12.89 | 12.89 | 12.89 | 12.89 | 13.29 | 13.29 | 13.49 | 13.29 | 14.32 | 14.32 | 14.32 | 14.32 |
| S/T | 0.73 | 0.83 | 0.92 | 1.00 | 0.59 | 0.67 | 0.76 | 0.85 | 0.52 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 4.57 | 4.57 | 4.57 | 4.57 | 4.58 | 4.58 | 4.58 | 4.58 | 4.59 | 4.59 | 4.60 | 4.59 | 4.62 | 4.62 | 4.62 | 4.62 |
| 40 | TC | 11.40 | 11.40 | 11.51 | 11.62 | 12.13 | 12.13 | 12.13 | 12.18 | 12.52 | 12.52 | 12.63 | 12.52 | 13.52 | 13.52 | 13.52 | 13.52 |
| S/T | 0.76 | 0.86 | 0.96 | 1.00 | 0.60 | 0.69 | 0.79 | 0.88 | 0.52 | 0.61 | 0.71 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 5.05 | 5.05 | 5.05 | 5.05 | 5.06 | 5.06 | 5.06 | 5.06 | 5.08 | 5.08 | 5.08 | 5.08 | 5.11 | 5.11 | 5.11 | 5.11 |
| 46 | TC | 10.55 | 10.55 | 10.67 | 10.78 | 11.24 | 11.24 | 11.24 | 11.35 | 11.61 | 11.61 | 11.61 | 11.61 | 12.59 | 12.59 | 12.59 | 12.59 |
| S/T | 0.77 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 5.61 | 5.61 | 5.61 | 5.61 | 5.63 | 5.63 | 5.63 | 5.63 | 5.65 | 5.65 | 5.65 | 5.65 | 5.70 | 5.70 | 5.70 | 5.70 |
| 50 | TC | 9.89 | 9.98 | 10.06 | 10.18 | 10.58 | 10.58 | 10.58 | 10.69 | 10.92 | 10.92 | 10.92 | 10.92 | 11.84 | 11.84 | 11.84 | 11.84 |
| S/T | 0.78 | 0.89 | 1.00 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 6.07 | 6.07 | 6.07 | 6.07 | 6.10 | 6.10 | 6.10 | 6.10 | 6.12 | 6.12 | 6.12 | 6.12 | 6.17 | 6.17 | 6.17 | 6.17 |
| 2040 | -15 | TC | 15.02 | 15.02 | 15.17 | 15.33 | 15.79 | 15.79 | 15.79 | 15.79 | 16.17 | 16.17 | 16.17 | 16.17 | 17.19 | 17.19 | 17.19 | 17.19 |
| S/T | 0.71 | 0.81 | 0.98 | 1.00 | 0.57 | 0.66 | 0.74 | 0.83 | 0.50 | 0.59 | 0.67 | 0.75 | 0.35 | 0.42 | 0.50 | 0.58 |
| PI | 3.26 | 3.26 | 3.26 | 3.26 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.24 | 3.24 | 3.24 | 3.24 |
| -10 | TC | 14.94 | 14.94 | 15.08 | 15.23 | 15.71 | 15.71 | 15.71 | 15.71 | 16.09 | 16.09 | 16.09 | 16.09 | 17.13 | 17.13 | 17.13 | 17.13 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.57 | 0.66 | 0.75 | 0.83 | 0.50 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 3.24 | 3.24 | 3.24 | 3.24 | 3.25 | 3.25 | 3.25 | 3.25 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 |
| -5 | TC | 14.85 | 14.85 | 14.99 | 15.14 | 15.65 | 15.65 | 15.65 | 15.65 | 16.03 | 16.03 | 16.03 | 16.03 | 17.09 | 17.09 | 17.09 | 17.09 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.25 | 3.25 | 3.25 | 3.25 |
| 0 | TC | 14.77 | 14.77 | 14.92 | 15.07 | 15.59 | 15.59 | 15.59 | 15.59 | 15.99 | 15.99 | 15.99 | 15.99 | 17.07 | 17.07 | 17.07 | 17.07 |
| S/T | 0.73 | 0.82 | 1.00 | 1.00 | 0.58 | 0.67 | 0.75 | 0.84 | 0.51 | 0.60 | 0.68 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.26 | 3.26 | 3.26 | 3.26 |
| 5 | TC | 14.70 | 14.70 | 14.84 | 14.99 | 15.53 | 15.53 | 15.53 | 15.53 | 15.94 | 15.94 | 15.94 | 15.94 | 17.06 | 17.06 | 17.06 | 17.06 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 |
| 10 | TC | 14.61 | 14.61 | 14.75 | 14.90 | 15.45 | 15.45 | 15.45 | 15.45 | 15.87 | 15.87 | 15.87 | 15.87 | 17.01 | 17.01 | 17.01 | 17.01 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 3.34 | 3.34 | 3.34 | 3.34 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.32 | 3.32 | 3.32 | 3.32 |
| 15 | TC | 14.49 | 14.49 | 14.63 | 14.78 | 15.35 | 15.35 | 15.35 | 15.35 | 15.77 | 15.77 | 15.77 | 15.77 | 16.94 | 16.94 | 16.94 | 16.94 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 3.42 | 3.42 | 3.42 | 3.42 | 3.41 | 3.41 | 3.41 | 3.41 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 |
| 20 | TC | 14.33 | 14.33 | 14.47 | 14.61 | 15.19 | 15.19 | 15.19 | 15.19 | 15.62 | 15.62 | 15.62 | 15.62 | 16.80 | 16.80 | 16.80 | 16.80 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 3.54 | 3.54 | 3.54 | 3.54 | 3.53 | 3.53 | 3.53 | 3.53 | 3.52 | 3.52 | 3.52 | 3.52 | 3.50 | 3.50 | 3.50 | 3.50 |
| 25 | TC | 13.67 | 13.67 | 13.81 | 13.95 | 14.50 | 14.50 | 14.50 | 14.50 | 14.93 | 14.93 | 14.93 | 14.93 | 16.08 | 16.08 | 16.08 | 16.08 |
| S/T | 0.75 | 0.85 | 0.95 | 1.00 | 0.59 | 0.69 | 0.78 | 0.88 | 0.52 | 0.61 | 0.70 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 | 3.90 |
| 30 | TC | 13.01 | 13.01 | 13.15 | 13.29 | 13.84 | 13.84 | 13.84 | 13.98 | 14.27 | 14.27 | 14.27 | 14.27 | 15.36 | 15.36 | 15.36 | 15.36 |
| S/T | 0.76 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 4.27 | 4.27 | 4.27 | 4.27 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.30 | 4.30 | 4.30 | 4.30 |
| 35 | TC | 12.37 | 12.49 | 12.60 | 12.72 | 13.15 | 13.15 | 13.15 | 13.29 | 13.58 | 13.58 | 13.78 | 13.58 | 14.64 | 14.64 | 14.64 | 14.64 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.72 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 4.67 | 4.67 | 4.67 | 4.67 | 4.68 | 4.68 | 4.68 | 4.68 | 4.69 | 4.69 | 4.70 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 |
| 40 | TC | 11.55 | 11.66 | 11.78 | 11.89 | 12.31 | 12.31 | 12.31 | 12.44 | 12.71 | 12.71 | 12.82 | 12.71 | 13.72 | 13.72 | 13.72 | 13.72 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 5.16 | 5.16 | 5.16 | 5.16 | 5.17 | 5.17 | 5.17 | 5.17 | 5.18 | 5.18 | 5.19 | 5.18 | 5.21 | 5.21 | 5.21 | 5.21 |
| 46 | TC | 10.68 | 10.79 | 10.91 | 11.02 | 11.42 | 11.42 | 11.42 | 11.54 | 11.79 | 11.79 | 11.79 | 11.79 | 12.76 | 12.76 | 12.76 | 12.76 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.74 | 0.86 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 5.73 | 5.73 | 5.73 | 5.73 | 5.76 | 5.76 | 5.76 | 5.76 | 5.77 | 5.77 | 5.77 | 5.77 | 5.82 | 5.82 | 5.82 | 5.82 |
| 50 | TC | 10.03 | 10.14 | 10.25 | 10.37 | 10.74 | 10.74 | 10.85 | 10.97 | 11.08 | 11.08 | 11.08 | 11.19 | 12.02 | 12.02 | 12.02 | 12.02 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.54 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.91 |
| PI | 6.21 | 6.21 | 6.21 | 6.21 | 6.23 | 6.23 | 6.23 | 6.23 | 6.25 | 6.25 | 6.25 | 6.25 | 6.30 | 6.30 | 6.30 | 6.30 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2400 | -15 | TC | 15.33 | 15.33 | 15.48 | 15.63 | 16.12 | 16.12 | 16.12 | 16.27 | 16.53 | 16.53 | 16.53 | 16.53 | 17.54 | 17.54 | 17.54 | 17.54 |
| S/T | 0.74 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.78 | 0.98 | 0.51 | 0.61 | 0.70 | 0.80 | 0.34 | 0.42 | 0.51 | 0.61 |
| PI | 3.33 | 3.33 | 3.33 | 3.33 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.31 | 3.31 | 3.31 | 3.31 |
| -10 | TC | 15.23 | 15.23 | 15.38 | 15.53 | 16.03 | 16.03 | 16.03 | 16.18 | 16.45 | 16.45 | 16.45 | 16.45 | 17.48 | 17.48 | 17.48 | 17.48 |
| S/T | 0.75 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.98 | 0.51 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.51 | 0.61 |
| PI | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 |
| -5 | TC | 15.14 | 15.14 | 15.29 | 15.44 | 15.97 | 15.97 | 15.97 | 16.12 | 16.38 | 16.38 | 16.38 | 16.38 | 17.44 | 17.44 | 17.44 | 17.44 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.99 | 0.52 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.52 | 0.61 |
| PI | 3.31 | 3.31 | 3.31 | 3.31 | 3.30 | 3.30 | 3.30 | 3.30 | 3.31 | 3.31 | 3.31 | 3.31 | 3.32 | 3.32 | 3.32 | 3.32 |
| 0 | TC | 15.07 | 15.07 | 15.22 | 15.36 | 15.91 | 15.91 | 15.91 | 16.06 | 16.34 | 16.34 | 16.34 | 16.34 | 17.42 | 17.42 | 17.42 | 17.42 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.60 | 0.70 | 0.79 | 0.99 | 0.52 | 0.62 | 0.72 | 0.81 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 |
| 5 | TC | 14.99 | 14.99 | 15.14 | 15.29 | 15.85 | 15.85 | 15.85 | 16.00 | 16.29 | 16.29 | 16.29 | 16.29 | 17.41 | 17.41 | 17.41 | 17.41 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.36 | 3.36 | 3.36 | 3.36 |
| 10 | TC | 14.90 | 14.90 | 15.05 | 15.19 | 15.78 | 15.78 | 15.78 | 15.92 | 16.22 | 16.22 | 16.22 | 16.22 | 17.36 | 17.36 | 17.36 | 17.36 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.35 | 0.44 | 0.52 | 0.62 |
| PI | 3.41 | 3.41 | 3.41 | 3.41 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 | 3.40 |
| 15 | TC | 14.78 | 14.78 | 14.93 | 15.07 | 15.67 | 15.67 | 15.67 | 15.81 | 16.12 | 16.12 | 16.12 | 16.12 | 17.29 | 17.29 | 17.29 | 17.29 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.49 | 3.49 | 3.49 | 3.49 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.47 | 3.47 | 3.47 | 3.47 |
| 20 | TC | 14.61 | 14.61 | 14.76 | 14.90 | 15.50 | 15.50 | 15.50 | 15.65 | 15.96 | 15.96 | 15.96 | 15.96 | 17.14 | 17.14 | 17.14 | 17.14 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.61 | 3.61 | 3.61 | 3.61 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.60 | 3.58 | 3.58 | 3.58 | 3.58 |
| 25 | TC | 13.95 | 14.10 | 14.24 | 14.38 | 14.81 | 14.81 | 14.81 | 14.96 | 15.25 | 15.25 | 15.25 | 15.25 | 16.42 | 16.42 | 16.42 | 16.42 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.93 | 0.53 | 0.64 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 |
| 30 | TC | 13.29 | 13.44 | 13.58 | 13.72 | 14.13 | 14.13 | 14.13 | 14.27 | 14.56 | 14.56 | 14.56 | 14.56 | 15.68 | 15.68 | 15.68 | 15.68 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 4.36 | 4.36 | 4.36 | 4.36 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.39 | 4.39 | 4.39 | 4.39 |
| 35 | TC | 12.63 | 12.75 | 12.86 | 12.98 | 13.44 | 13.44 | 13.44 | 13.58 | 13.87 | 13.87 | 14.07 | 14.21 | 14.96 | 14.96 | 14.96 | 14.96 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 4.77 | 4.77 | 4.77 | 4.77 | 4.78 | 4.78 | 4.78 | 4.78 | 4.79 | 4.79 | 4.80 | 4.79 | 4.82 | 4.82 | 4.82 | 4.82 |
| 40 | TC | 11.79 | 11.91 | 12.02 | 12.14 | 12.57 | 12.57 | 12.62 | 12.75 | 12.97 | 12.97 | 13.08 | 13.21 | 14.01 | 14.01 | 14.01 | 14.01 |
| S/T | 0.85 | 0.99 | 1.00 | 1.00 | 0.64 | 0.78 | 0.90 | 1.00 | 0.55 | 0.68 | 0.80 | 0.93 | 0.33 | 0.45 | 0.57 | 0.90 |
| PI | 5.26 | 5.26 | 5.26 | 5.26 | 5.28 | 5.28 | 5.28 | 5.28 | 5.29 | 5.29 | 5.30 | 5.29 | 5.33 | 5.33 | 5.33 | 5.33 |
| 46 | TC | 10.91 | 11.02 | 11.14 | 11.25 | 11.65 | 11.65 | 11.76 | 11.88 | 12.02 | 12.02 | 12.02 | 12.13 | 13.02 | 13.02 | 13.02 | 13.02 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.65 | 0.79 | 0.92 | 1.00 | 0.55 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.57 | 0.92 |
| PI | 5.85 | 5.85 | 5.85 | 5.85 | 5.88 | 5.88 | 5.88 | 5.88 | 5.89 | 5.89 | 5.89 | 5.89 | 5.94 | 5.94 | 5.94 | 5.94 |
| 50 | TC | 10.25 | 10.37 | 10.48 | 10.60 | 10.97 | 10.97 | 11.08 | 11.19 | 11.31 | 11.31 | 11.31 | 11.42 | 12.28 | 12.28 | 12.28 | 12.28 |
| S/T | 0.89 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.95 | 1.00 | 0.56 | 0.70 | 0.85 | 0.98 | 0.33 | 0.46 | 0.59 | 0.97 |
| PI | 6.34 | 6.34 | 6.34 | 6.34 | 6.36 | 6.36 | 6.36 | 6.36 | 6.38 | 6.38 | 6.38 | 6.38 | 6.43 | 6.43 | 6.43 | 6.43 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS060D8S+38QUS060D8T | | | | | | | | | | | | | | | | | | |
| INDOOR AIRFLOW (CMH) | OUTDOOR DB(℃) | ID WB  (℃) | 16.0 | | | | 18.0 | | | | 19.0 | | | | 22.0 | | | |
| ID DB  (℃) | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 | 23.0 | 25.0 | 27.0 | 29.0 |
| 1820 | -15 | TC | 15.98 | 15.98 | 15.98 | 16.13 | 16.80 | 17.13 | 17.13 | 17.13 | 17.20 | 17.20 | 17.20 | 17.20 | 18.27 | 18.27 | 18.27 | 18.27 |
| S/T | 0.69 | 0.76 | 0.84 | 0.91 | 0.55 | 0.63 | 0.70 | 0.77 | 0.49 | 0.57 | 0.64 | 0.70 | 0.36 | 0.42 | 0.49 | 0.55 |
| PI | 3.50 | 3.51 | 3.51 | 3.50 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.48 | 3.48 | 3.48 | 3.48 |
| -10 | TC | 15.88 | 15.88 | 15.88 | 16.03 | 16.71 | 17.04 | 17.04 | 17.04 | 17.12 | 17.12 | 17.12 | 17.12 | 18.21 | 18.21 | 18.21 | 18.21 |
| S/T | 0.69 | 0.77 | 0.84 | 0.91 | 0.55 | 0.63 | 0.71 | 0.78 | 0.49 | 0.57 | 0.64 | 0.71 | 0.36 | 0.43 | 0.49 | 0.55 |
| PI | 3.49 | 3.49 | 3.49 | 3.49 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 |
| -5 | TC | 15.79 | 15.79 | 15.79 | 15.94 | 16.64 | 16.97 | 16.97 | 16.97 | 17.05 | 17.05 | 17.05 | 17.05 | 18.16 | 18.16 | 18.16 | 18.16 |
| S/T | 0.69 | 0.77 | 0.85 | 0.92 | 0.56 | 0.63 | 0.71 | 0.78 | 0.50 | 0.58 | 0.64 | 0.71 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.48 | 3.49 | 3.49 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.49 | 3.49 | 3.49 | 3.49 |
| 0 | TC | 15.71 | 15.71 | 15.71 | 15.86 | 16.58 | 16.91 | 16.91 | 16.91 | 17.01 | 17.01 | 17.01 | 17.01 | 18.14 | 18.14 | 18.14 | 18.14 |
| S/T | 0.70 | 0.77 | 0.85 | 0.92 | 0.56 | 0.64 | 0.72 | 0.78 | 0.50 | 0.58 | 0.65 | 0.72 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.50 | 3.50 | 3.50 | 3.50 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.50 | 3.50 | 3.50 | 3.50 |
| 5 | TC | 15.63 | 15.63 | 15.63 | 15.78 | 16.52 | 16.85 | 16.85 | 16.85 | 16.95 | 16.95 | 16.95 | 16.95 | 18.13 | 18.13 | 18.13 | 18.13 |
| S/T | 0.70 | 0.78 | 0.86 | 0.93 | 0.56 | 0.64 | 0.72 | 0.79 | 0.50 | 0.58 | 0.65 | 0.72 | 0.36 | 0.43 | 0.50 | 0.56 |
| PI | 3.53 | 3.53 | 3.53 | 3.53 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.53 | 3.53 | 3.53 | 3.53 |
| 10 | TC | 15.53 | 15.53 | 15.53 | 15.68 | 16.44 | 16.77 | 16.77 | 16.77 | 16.88 | 16.88 | 16.88 | 16.88 | 18.08 | 18.08 | 18.08 | 18.08 |
| S/T | 0.70 | 0.78 | 0.86 | 0.93 | 0.56 | 0.64 | 0.72 | 0.79 | 0.50 | 0.58 | 0.65 | 0.72 | 0.37 | 0.44 | 0.50 | 0.56 |
| PI | 3.59 | 3.59 | 3.59 | 3.59 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.57 | 3.57 | 3.57 | 3.57 |
| 15 | TC | 15.41 | 15.41 | 15.41 | 15.55 | 16.33 | 16.65 | 16.65 | 16.65 | 16.78 | 16.78 | 16.78 | 16.78 | 18.01 | 18.01 | 18.01 | 18.01 |
| S/T | 0.71 | 0.79 | 0.87 | 0.94 | 0.57 | 0.65 | 0.73 | 0.80 | 0.51 | 0.59 | 0.66 | 0.73 | 0.37 | 0.44 | 0.51 | 0.57 |
| PI | 3.67 | 3.68 | 3.68 | 3.67 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.65 | 3.65 | 3.65 | 3.65 |
| 20 | TC | 15.23 | 15.23 | 15.23 | 15.38 | 16.15 | 16.15 | 16.15 | 16.15 | 16.61 | 16.61 | 16.61 | 16.61 | 17.85 | 17.85 | 17.85 | 17.85 |
| S/T | 0.71 | 0.79 | 0.87 | 0.94 | 0.57 | 0.65 | 0.73 | 0.80 | 0.51 | 0.59 | 0.66 | 0.73 | 0.37 | 0.44 | 0.51 | 0.57 |
| PI | 3.80 | 3.81 | 3.81 | 3.80 | 3.79 | 3.79 | 3.79 | 3.79 | 3.78 | 3.78 | 3.78 | 3.78 | 3.76 | 3.76 | 3.76 | 3.76 |
| 25 | TC | 14.54 | 14.54 | 14.54 | 14.69 | 15.44 | 15.44 | 15.44 | 15.44 | 15.90 | 15.90 | 15.90 | 15.90 | 17.10 | 17.10 | 17.10 | 17.10 |
| S/T | 0.72 | 0.80 | 0.88 | 0.96 | 0.58 | 0.66 | 0.74 | 0.81 | 0.51 | 0.59 | 0.67 | 0.74 | 0.37 | 0.44 | 0.51 | 0.58 |
| PI | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 | 4.19 |
| 30 | TC | 13.85 | 13.85 | 14.00 | 14.14 | 14.72 | 14.72 | 14.72 | 14.72 | 15.18 | 15.18 | 15.18 | 15.18 | 16.36 | 16.36 | 16.36 | 16.36 |
| S/T | 0.72 | 0.81 | 0.90 | 0.98 | 0.58 | 0.66 | 0.75 | 0.83 | 0.51 | 0.59 | 0.68 | 0.76 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 4.59 | 4.59 | 4.59 | 4.59 | 4.60 | 4.60 | 4.60 | 4.60 | 4.60 | 4.60 | 4.60 | 4.60 | 4.62 | 4.62 | 4.62 | 4.62 |
| 35 | TC | 13.17 | 13.17 | 13.31 | 13.45 | 14.00 | 14.00 | 14.00 | 14.00 | 14.43 | 14.43 | 14.66 | 14.43 | 15.58 | 15.58 | 15.58 | 15.58 |
| S/T | 0.73 | 0.83 | 0.92 | 1.00 | 0.59 | 0.67 | 0.76 | 0.85 | 0.52 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 5.01 | 5.01 | 5.01 | 5.01 | 5.03 | 5.03 | 5.03 | 5.03 | 5.04 | 5.04 | 5.05 | 5.04 | 5.08 | 5.08 | 5.08 | 5.08 |
| 40 | TC | 12.41 | 12.41 | 12.54 | 12.67 | 13.22 | 13.22 | 13.22 | 13.27 | 13.64 | 13.64 | 13.76 | 13.64 | 14.74 | 14.74 | 14.74 | 14.74 |
| S/T | 0.76 | 0.86 | 0.96 | 1.00 | 0.60 | 0.69 | 0.79 | 0.88 | 0.52 | 0.61 | 0.71 | 0.80 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 5.54 | 5.54 | 5.54 | 5.54 | 5.56 | 5.56 | 5.56 | 5.56 | 5.57 | 5.57 | 5.58 | 5.57 | 5.61 | 5.61 | 5.61 | 5.61 |
| 46 | TC | 11.49 | 11.49 | 11.60 | 11.72 | 12.26 | 12.26 | 12.26 | 12.38 | 12.67 | 12.67 | 12.67 | 12.67 | 13.70 | 13.70 | 13.70 | 13.70 |
| S/T | 0.77 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.90 | 0.52 | 0.62 | 0.72 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 6.16 | 6.16 | 6.16 | 6.16 | 6.18 | 6.18 | 6.18 | 6.18 | 6.20 | 6.20 | 6.20 | 6.20 | 6.25 | 6.25 | 6.25 | 6.25 |
| 50 | TC | 10.77 | 10.88 | 11.00 | 11.11 | 11.51 | 11.51 | 11.51 | 11.63 | 11.92 | 11.92 | 11.92 | 11.92 | 12.90 | 12.90 | 12.90 | 12.90 |
| S/T | 0.78 | 0.89 | 1.00 | 1.00 | 0.61 | 0.71 | 0.82 | 0.92 | 0.53 | 0.63 | 0.73 | 0.84 | 0.34 | 0.44 | 0.53 | 0.63 |
| PI | 6.67 | 6.67 | 6.67 | 6.67 | 6.70 | 6.70 | 6.70 | 6.70 | 6.71 | 6.71 | 6.71 | 6.71 | 6.77 | 6.77 | 6.77 | 6.77 |
| 2210 | -15 | TC | 16.28 | 16.28 | 16.43 | 16.59 | 17.13 | 17.13 | 17.13 | 17.13 | 17.57 | 17.57 | 17.57 | 17.57 | 18.66 | 18.66 | 18.66 | 18.66 |
| S/T | 0.71 | 0.81 | 0.98 | 1.00 | 0.57 | 0.66 | 0.74 | 0.83 | 0.50 | 0.59 | 0.67 | 0.75 | 0.35 | 0.42 | 0.50 | 0.58 |
| PI | 3.57 | 3.57 | 3.57 | 3.57 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 |
| -10 | TC | 16.19 | 16.19 | 16.34 | 16.49 | 17.04 | 17.04 | 17.04 | 17.04 | 17.48 | 17.48 | 17.48 | 17.48 | 18.59 | 18.59 | 18.59 | 18.59 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.57 | 0.66 | 0.75 | 0.83 | 0.50 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.50 | 0.58 |
| PI | 3.55 | 3.55 | 3.55 | 3.55 | 3.54 | 3.54 | 3.54 | 3.54 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 |
| -5 | TC | 16.09 | 16.09 | 16.24 | 16.39 | 16.97 | 16.97 | 16.97 | 16.97 | 17.41 | 17.41 | 17.41 | 17.41 | 18.55 | 18.55 | 18.55 | 18.55 |
| S/T | 0.72 | 0.82 | 0.99 | 1.00 | 0.58 | 0.66 | 0.75 | 0.84 | 0.51 | 0.59 | 0.67 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 |
| 0 | TC | 16.01 | 16.01 | 16.16 | 16.31 | 16.91 | 16.91 | 16.91 | 16.91 | 17.37 | 17.37 | 17.37 | 17.37 | 18.53 | 18.53 | 18.53 | 18.53 |
| S/T | 0.73 | 0.82 | 1.00 | 1.00 | 0.58 | 0.67 | 0.75 | 0.84 | 0.51 | 0.60 | 0.68 | 0.76 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.56 | 3.56 | 3.56 | 3.56 | 3.55 | 3.55 | 3.55 | 3.55 | 3.56 | 3.56 | 3.56 | 3.56 | 3.57 | 3.57 | 3.57 | 3.57 |
| 5 | TC | 15.93 | 15.93 | 16.08 | 16.23 | 16.85 | 16.85 | 16.85 | 16.85 | 17.31 | 17.31 | 17.31 | 17.31 | 18.52 | 18.52 | 18.52 | 18.52 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.35 | 0.43 | 0.51 | 0.59 |
| PI | 3.59 | 3.59 | 3.59 | 3.59 | 3.58 | 3.58 | 3.58 | 3.58 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 |
| 10 | TC | 15.83 | 15.83 | 15.98 | 16.13 | 16.77 | 16.77 | 16.77 | 16.77 | 17.24 | 17.24 | 17.24 | 17.24 | 18.47 | 18.47 | 18.47 | 18.47 |
| S/T | 0.73 | 0.83 | 1.00 | 1.00 | 0.58 | 0.67 | 0.76 | 0.85 | 0.51 | 0.60 | 0.68 | 0.77 | 0.36 | 0.44 | 0.51 | 0.59 |
| PI | 3.65 | 3.65 | 3.65 | 3.65 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 |
| 15 | TC | 15.70 | 15.70 | 15.85 | 16.00 | 16.65 | 16.65 | 16.65 | 16.65 | 17.13 | 17.13 | 17.13 | 17.13 | 18.39 | 18.39 | 18.39 | 18.39 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 3.74 | 3.74 | 3.74 | 3.74 | 3.72 | 3.72 | 3.72 | 3.72 | 3.73 | 3.73 | 3.73 | 3.73 | 3.72 | 3.72 | 3.72 | 3.72 |
| 20 | TC | 15.53 | 15.53 | 15.67 | 15.82 | 16.48 | 16.48 | 16.48 | 16.48 | 16.97 | 16.97 | 16.97 | 16.97 | 18.23 | 18.23 | 18.23 | 18.23 |
| S/T | 0.74 | 0.84 | 0.93 | 1.00 | 0.59 | 0.68 | 0.77 | 0.86 | 0.52 | 0.61 | 0.69 | 0.78 | 0.36 | 0.44 | 0.52 | 0.60 |
| PI | 3.87 | 3.87 | 3.87 | 3.87 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.83 | 3.83 | 3.83 | 3.83 |
| 25 | TC | 14.81 | 14.81 | 14.95 | 15.10 | 15.73 | 15.73 | 15.73 | 15.73 | 16.22 | 16.22 | 16.22 | 16.22 | 17.45 | 17.45 | 17.45 | 17.45 |
| S/T | 0.75 | 0.85 | 0.95 | 1.00 | 0.59 | 0.69 | 0.78 | 0.88 | 0.52 | 0.61 | 0.70 | 0.79 | 0.35 | 0.44 | 0.52 | 0.61 |
| PI | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 |
| 30 | TC | 14.12 | 14.12 | 14.26 | 14.41 | 15.01 | 15.01 | 15.01 | 15.15 | 15.47 | 15.47 | 15.47 | 15.47 | 16.68 | 16.68 | 16.68 | 16.68 |
| S/T | 0.76 | 0.87 | 0.97 | 1.00 | 0.60 | 0.70 | 0.80 | 0.89 | 0.52 | 0.62 | 0.71 | 0.81 | 0.35 | 0.44 | 0.53 | 0.62 |
| PI | 4.67 | 4.67 | 4.67 | 4.67 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.70 | 4.70 | 4.70 | 4.70 |
| 35 | TC | 13.40 | 13.54 | 13.69 | 13.83 | 14.29 | 14.29 | 14.29 | 14.44 | 14.72 | 14.72 | 14.95 | 14.72 | 15.87 | 15.87 | 15.87 | 15.87 |
| S/T | 0.78 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.72 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 5.10 | 5.10 | 5.10 | 5.10 | 5.12 | 5.12 | 5.12 | 5.12 | 5.13 | 5.13 | 5.14 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 |
| 40 | TC | 12.48 | 12.61 | 12.74 | 12.87 | 13.31 | 13.31 | 13.31 | 13.44 | 13.72 | 13.72 | 13.85 | 13.72 | 14.82 | 14.82 | 14.82 | 14.82 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 5.63 | 5.63 | 5.63 | 5.63 | 5.65 | 5.65 | 5.65 | 5.65 | 5.66 | 5.66 | 5.67 | 5.66 | 5.69 | 5.69 | 5.69 | 5.69 |
| 46 | TC | 11.57 | 11.68 | 11.79 | 11.91 | 12.33 | 12.33 | 12.33 | 12.45 | 12.73 | 12.73 | 12.73 | 12.73 | 13.78 | 13.78 | 13.78 | 13.78 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.75 | 0.86 | 0.98 | 0.54 | 0.65 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 6.26 | 6.26 | 6.26 | 6.26 | 6.29 | 6.29 | 6.29 | 6.29 | 6.30 | 6.30 | 6.30 | 6.30 | 6.36 | 6.36 | 6.36 | 6.36 |
| 50 | TC | 10.86 | 10.97 | 11.08 | 11.20 | 11.60 | 11.60 | 11.71 | 11.82 | 11.99 | 11.99 | 11.99 | 12.11 | 12.99 | 12.99 | 12.99 | 12.99 |
| S/T | 0.84 | 0.97 | 1.00 | 1.00 | 0.64 | 0.76 | 0.89 | 1.00 | 0.54 | 0.67 | 0.79 | 0.91 | 0.33 | 0.45 | 0.56 | 0.91 |
| PI | 6.78 | 6.78 | 6.78 | 6.78 | 6.81 | 6.81 | 6.81 | 6.81 | 6.83 | 6.83 | 6.83 | 6.83 | 6.88 | 6.88 | 6.88 | 6.88 |

**Specifications**

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2600 | -15 | TC | 16.62 | 16.62 | 16.80 | 16.98 | 17.46 | 17.46 | 17.46 | 17.64 | 17.89 | 17.89 | 17.89 | 17.89 | 19.01 | 19.01 | 19.01 | 19.01 |
| S/T | 0.74 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.78 | 0.98 | 0.51 | 0.61 | 0.70 | 0.80 | 0.34 | 0.42 | 0.51 | 0.61 |
| PI | 3.64 | 3.64 | 3.64 | 3.64 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.62 | 3.62 | 3.62 | 3.62 |
| -10 | TC | 16.52 | 16.52 | 16.70 | 16.88 | 17.37 | 17.37 | 17.37 | 17.54 | 17.80 | 17.80 | 17.80 | 17.80 | 18.95 | 18.95 | 18.95 | 18.95 |
| S/T | 0.75 | 0.85 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.98 | 0.51 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.51 | 0.61 |
| PI | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 |
| -5 | TC | 16.42 | 16.42 | 16.60 | 16.78 | 17.30 | 17.30 | 17.30 | 17.48 | 17.74 | 17.74 | 17.74 | 17.74 | 18.90 | 18.90 | 18.90 | 18.90 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.59 | 0.69 | 0.79 | 0.99 | 0.52 | 0.61 | 0.71 | 0.81 | 0.34 | 0.43 | 0.52 | 0.61 |
| PI | 3.61 | 3.61 | 3.61 | 3.61 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.63 | 3.63 | 3.63 | 3.63 |
| 0 | TC | 16.34 | 16.34 | 16.51 | 16.69 | 17.23 | 17.23 | 17.23 | 17.41 | 17.69 | 17.69 | 17.69 | 17.69 | 18.88 | 18.88 | 18.88 | 18.88 |
| S/T | 0.75 | 0.86 | 1.00 | 1.00 | 0.60 | 0.70 | 0.79 | 0.99 | 0.52 | 0.62 | 0.72 | 0.81 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.64 | 3.64 | 3.64 | 3.64 |
| 5 | TC | 16.25 | 16.25 | 16.43 | 16.61 | 17.17 | 17.17 | 17.17 | 17.35 | 17.63 | 17.63 | 17.63 | 17.63 | 18.87 | 18.87 | 18.87 | 18.87 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.34 | 0.43 | 0.52 | 0.62 |
| PI | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.67 | 3.67 | 3.67 | 3.67 |
| 10 | TC | 16.16 | 16.16 | 16.33 | 16.51 | 17.09 | 17.09 | 17.09 | 17.26 | 17.56 | 17.56 | 17.56 | 17.56 | 18.82 | 18.82 | 18.82 | 18.82 |
| S/T | 0.76 | 0.87 | 1.00 | 1.00 | 0.60 | 0.70 | 0.80 | 1.00 | 0.52 | 0.62 | 0.72 | 0.82 | 0.35 | 0.44 | 0.52 | 0.62 |
| PI | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 |
| 15 | TC | 16.02 | 16.02 | 16.20 | 16.37 | 16.97 | 16.97 | 16.97 | 17.15 | 17.45 | 17.45 | 17.45 | 17.45 | 18.74 | 18.74 | 18.74 | 18.74 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.80 | 3.80 | 3.80 | 3.80 | 3.79 | 3.79 | 3.79 | 3.79 |
| 20 | TC | 15.84 | 15.84 | 16.02 | 16.19 | 16.79 | 16.79 | 16.79 | 16.97 | 17.28 | 17.28 | 17.28 | 17.28 | 18.58 | 18.58 | 18.58 | 18.58 |
| S/T | 0.77 | 0.88 | 0.99 | 1.00 | 0.61 | 0.71 | 0.81 | 0.91 | 0.53 | 0.63 | 0.73 | 0.83 | 0.35 | 0.44 | 0.53 | 0.63 |
| PI | 3.95 | 3.95 | 3.95 | 3.95 | 3.94 | 3.94 | 3.94 | 3.94 | 3.93 | 3.93 | 3.93 | 3.93 | 3.91 | 3.91 | 3.91 | 3.91 |
| 25 | TC | 15.10 | 15.24 | 15.38 | 15.53 | 16.05 | 16.05 | 16.05 | 16.22 | 16.53 | 16.53 | 16.53 | 16.53 | 17.77 | 17.77 | 17.77 | 17.77 |
| S/T | 0.79 | 0.90 | 1.00 | 1.00 | 0.61 | 0.72 | 0.83 | 0.93 | 0.53 | 0.64 | 0.74 | 0.85 | 0.34 | 0.44 | 0.54 | 0.64 |
| PI | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 |
| 30 | TC | 14.41 | 14.55 | 14.69 | 14.84 | 15.30 | 15.30 | 15.30 | 15.44 | 15.79 | 15.79 | 15.79 | 15.79 | 16.99 | 16.99 | 16.99 | 16.99 |
| S/T | 0.80 | 0.92 | 1.00 | 1.00 | 0.62 | 0.73 | 0.85 | 0.96 | 0.53 | 0.64 | 0.76 | 0.87 | 0.34 | 0.44 | 0.54 | 0.65 |
| PI | 4.77 | 4.77 | 4.77 | 4.77 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.80 | 4.80 | 4.80 | 4.80 |
| 35 | TC | 13.66 | 13.80 | 13.95 | 14.09 | 14.55 | 14.55 | 14.55 | 14.69 | 15.01 | 15.01 | 15.24 | 15.38 | 16.19 | 16.19 | 16.19 | 16.19 |
| S/T | 0.82 | 0.94 | 1.00 | 1.00 | 0.63 | 0.75 | 0.87 | 0.98 | 0.54 | 0.66 | 0.77 | 0.88 | 0.34 | 0.44 | 0.55 | 0.66 |
| PI | 5.21 | 5.21 | 5.21 | 5.21 | 5.23 | 5.23 | 5.23 | 5.23 | 5.24 | 5.24 | 5.25 | 5.24 | 5.28 | 5.28 | 5.28 | 5.28 |
| 40 | TC | 12.72 | 12.85 | 12.98 | 13.11 | 13.57 | 13.57 | 13.62 | 13.75 | 14.00 | 14.00 | 14.12 | 14.26 | 15.12 | 15.12 | 15.12 | 15.12 |
| S/T | 0.85 | 0.99 | 1.00 | 1.00 | 0.65 | 0.78 | 0.90 | 1.00 | 0.55 | 0.68 | 0.80 | 0.93 | 0.33 | 0.45 | 0.57 | 0.90 |
| PI | 5.75 | 5.75 | 5.75 | 5.75 | 5.77 | 5.77 | 5.77 | 5.77 | 5.78 | 5.78 | 5.79 | 5.78 | 5.83 | 5.83 | 5.83 | 5.83 |
| 46 | TC | 11.79 | 11.91 | 12.02 | 12.14 | 12.59 | 12.59 | 12.70 | 12.82 | 12.99 | 12.99 | 12.99 | 13.13 | 14.07 | 14.07 | 14.07 | 14.07 |
| S/T | 0.87 | 1.00 | 1.00 | 1.00 | 0.65 | 0.79 | 0.92 | 1.00 | 0.55 | 0.69 | 0.82 | 0.95 | 0.33 | 0.45 | 0.57 | 0.92 |
| PI | 6.39 | 6.39 | 6.39 | 6.39 | 6.42 | 6.42 | 6.42 | 6.42 | 6.44 | 6.44 | 6.44 | 6.44 | 6.49 | 6.49 | 6.49 | 6.49 |
| 50 | TC | 11.06 | 11.17 | 11.28 | 11.40 | 11.82 | 11.82 | 11.94 | 12.05 | 12.22 | 12.22 | 12.22 | 12.33 | 13.24 | 13.24 | 13.24 | 13.24 |
| S/T | 0.90 | 1.00 | 1.00 | 1.00 | 0.67 | 0.81 | 0.95 | 1.00 | 0.56 | 0.70 | 0.85 | 0.98 | 0.33 | 0.46 | 0.59 | 0.97 |
| PI | 6.92 | 6.92 | 6.92 | 6.92 | 6.95 | 6.95 | 6.95 | 6.95 | 6.97 | 6.97 | 6.97 | 6.97 | 7.03 | 7.03 | 7.03 | 7.03 |

TC:Total Cooling Capacity (kW)

S/T:Sensible Cooling Capacity Ratio

PI:Power Input(kW)

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

**Heating**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS012D8S-1+38QUS012D8S-1 | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 300 | -15.0 | 2.61 | 2.59 | 2.59 | 2.56 | 1.17 | 1.21 | 1.18 | 1.19 |
| -10.0 | 2.79 | 2.76 | 2.76 | 2.74 | 1.25 | 1.29 | 1.26 | 1.27 |
| -7.0 | 2.92 | 2.90 | 2.90 | 2.87 | 1.32 | 1.37 | 1.34 | 1.35 |
| -5.6 | 2.98 | 2.95 | 2.95 | 2.92 | 1.29 | 1.30 | 1.31 | 1.31 |
| -2.8 | 3.04 | 3.01 | 3.01 | 2.98 | 1.23 | 1.24 | 1.24 | 1.25 |
| 0.0 | 3.07 | 3.04 | 3.01 | 3.01 | 1.17 | 1.17 | 1.18 | 1.18 |
| 2.8 | 3.21 | 3.18 | 3.16 | 3.13 | 1.12 | 1.13 | 1.13 | 1.13 |
| 5.6 | 3.45 | 3.42 | 3.39 | 3.36 | 1.07 | 1.07 | 1.08 | 1.08 |
| 7.0 | 3.73 | 3.69 | 3.61 | 3.61 | 1.05 | 1.02 | 1.05 | 1.05 |
| 11.1 | 3.90 | 3.84 | 3.81 | 3.78 | 0.96 | 0.96 | 0.96 | 0.96 |
| 13.9 | 4.01 | 3.98 | 3.96 | 3.93 | 0.91 | 0.90 | 0.90 | 0.90 |
| 16.7 | 4.16 | 4.10 | 4.07 | 4.04 | 0.85 | 0.84 | 0.84 | 0.83 |
| 18.0 | 4.22 | 4.16 | 4.13 | 4.10 | 0.82 | 0.81 | 0.81 | 0.80 |
| 480 | -15.0 | 2.66 | 2.63 | 2.63 | 2.61 | 1.18 | 1.22 | 1.20 | 1.20 |
| -10.0 | 2.84 | 2.81 | 2.81 | 2.78 | 1.25 | 1.30 | 1.28 | 1.28 |
| -7.0 | 2.97 | 2.95 | 2.95 | 2.92 | 1.33 | 1.38 | 1.36 | 1.36 |
| -5.6 | 3.04 | 3.01 | 3.01 | 2.98 | 1.30 | 1.31 | 1.32 | 1.33 |
| -2.8 | 3.13 | 3.07 | 3.07 | 3.04 | 1.24 | 1.25 | 1.25 | 1.26 |
| 0.0 | 3.16 | 3.10 | 3.07 | 3.07 | 1.17 | 1.18 | 1.19 | 1.19 |
| 2.8 | 3.27 | 3.24 | 3.21 | 3.18 | 1.13 | 1.14 | 1.14 | 1.14 |
| 5.6 | 3.53 | 3.50 | 3.47 | 3.45 | 1.08 | 1.08 | 1.08 | 1.09 |
| 7.0 | 3.81 | 3.78 | 3.69 | 3.69 | 1.06 | 1.03 | 1.06 | 1.06 |
| 11.1 | 3.98 | 3.93 | 3.90 | 3.87 | 0.97 | 0.97 | 0.97 | 0.97 |
| 13.9 | 4.13 | 4.07 | 4.04 | 4.01 | 0.91 | 0.91 | 0.91 | 0.90 |
| 16.7 | 4.28 | 4.22 | 4.19 | 4.16 | 0.86 | 0.85 | 0.84 | 0.84 |
| 18.0 | 4.33 | 4.28 | 4.25 | 4.22 | 0.83 | 0.82 | 0.81 | 0.81 |
| 600 | -15.0 | 2.69 | 2.67 | 2.67 | 2.64 | 1.19 | 1.24 | 1.21 | 1.22 |
| -10.0 | 2.87 | 2.85 | 2.85 | 2.82 | 1.27 | 1.32 | 1.29 | 1.30 |
| -7.0 | 3.01 | 2.98 | 2.98 | 2.95 | 1.35 | 1.40 | 1.37 | 1.38 |
| -5.6 | 3.07 | 3.04 | 3.04 | 3.01 | 1.32 | 1.33 | 1.34 | 1.34 |
| -2.8 | 3.16 | 3.10 | 3.10 | 3.07 | 1.25 | 1.26 | 1.27 | 1.27 |
| 0.0 | 3.18 | 3.13 | 3.13 | 3.10 | 1.19 | 1.20 | 1.20 | 1.20 |
| 2.8 | 3.30 | 3.27 | 3.24 | 3.21 | 1.15 | 1.15 | 1.15 | 1.16 |
| 5.6 | 3.56 | 3.53 | 3.50 | 3.47 | 1.09 | 1.10 | 1.10 | 1.10 |
| 7.0 | 3.84 | 3.81 | 3.72 | 3.72 | 1.07 | 1.04 | 1.07 | 1.07 |
| 11.1 | 4.01 | 3.96 | 3.93 | 3.90 | 0.98 | 0.98 | 0.98 | 0.98 |
| 13.9 | 4.16 | 4.10 | 4.07 | 4.04 | 0.92 | 0.92 | 0.92 | 0.91 |
| 16.7 | 4.30 | 4.25 | 4.22 | 4.16 | 0.87 | 0.86 | 0.85 | 0.85 |
| 18.0 | 4.36 | 4.30 | 4.28 | 4.25 | 0.84 | 0.83 | 0.82 | 0.82 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS018D8S-1+38QUS018D8S-1 | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 515 | -15.0 | 3.93 | 3.87 | 3.85 | 3.82 | 1.45 | 1.50 | 1.49 | 1.50 |
| -10.0 | 4.19 | 4.14 | 4.11 | 4.08 | 1.55 | 1.60 | 1.59 | 1.60 |
| -7.0 | 4.39 | 4.33 | 4.31 | 4.28 | 1.64 | 1.70 | 1.69 | 1.70 |
| -5.6 | 4.48 | 4.42 | 4.39 | 4.36 | 1.62 | 1.65 | 1.66 | 1.67 |
| -2.8 | 4.54 | 4.48 | 4.45 | 4.45 | 1.57 | 1.60 | 1.61 | 1.63 |
| 0.0 | 4.57 | 4.51 | 4.48 | 4.45 | 1.53 | 1.56 | 1.57 | 1.58 |
| 2.8 | 4.74 | 4.68 | 4.65 | 4.63 | 1.51 | 1.53 | 1.54 | 1.55 |
| 5.6 | 5.09 | 5.03 | 5.00 | 4.97 | 1.48 | 1.50 | 1.52 | 1.53 |
| 7.0 | 5.46 | 5.39 | 5.31 | 5.25 | 1.46 | 1.47 | 1.49 | 1.50 |
| 11.1 | 5.68 | 5.60 | 5.57 | 5.51 | 1.41 | 1.43 | 1.44 | 1.44 |
| 13.9 | 5.86 | 5.77 | 5.74 | 5.68 | 1.37 | 1.39 | 1.40 | 1.41 |
| 16.7 | 6.03 | 5.95 | 5.92 | 5.86 | 1.34 | 1.35 | 1.36 | 1.37 |
| 18.0 | 6.12 | 6.03 | 6.00 | 5.95 | 1.32 | 1.33 | 1.34 | 1.35 |
| 706 | -15.0 | 4.00 | 3.95 | 3.92 | 3.90 | 1.47 | 1.51 | 1.50 | 1.52 |
| -10.0 | 4.27 | 4.22 | 4.19 | 4.16 | 1.57 | 1.62 | 1.60 | 1.62 |
| -7.0 | 4.48 | 4.42 | 4.39 | 4.36 | 1.66 | 1.72 | 1.70 | 1.72 |
| -5.6 | 4.57 | 4.51 | 4.48 | 4.45 | 1.63 | 1.66 | 1.67 | 1.69 |
| -2.8 | 4.63 | 4.57 | 4.57 | 4.54 | 1.59 | 1.62 | 1.63 | 1.64 |
| 0.0 | 4.65 | 4.60 | 4.57 | 4.54 | 1.55 | 1.57 | 1.58 | 1.60 |
| 2.8 | 4.86 | 4.80 | 4.77 | 4.71 | 1.53 | 1.54 | 1.55 | 1.57 |
| 5.6 | 5.21 | 5.15 | 5.12 | 5.06 | 1.50 | 1.52 | 1.53 | 1.54 |
| 7.0 | 5.57 | 5.51 | 5.39 | 5.37 | 1.48 | 1.49 | 1.51 | 1.52 |
| 11.1 | 5.80 | 5.71 | 5.68 | 5.63 | 1.43 | 1.45 | 1.46 | 1.47 |
| 13.9 | 5.97 | 5.92 | 5.86 | 5.83 | 1.39 | 1.41 | 1.42 | 1.43 |
| 16.7 | 6.18 | 6.09 | 6.03 | 6.00 | 1.36 | 1.37 | 1.38 | 1.39 |
| 18.0 | 6.26 | 6.18 | 6.12 | 6.09 | 1.34 | 1.36 | 1.36 | 1.37 |
| 911 | -15.0 | 4.03 | 3.98 | 3.95 | 3.93 | 1.48 | 1.53 | 1.52 | 1.53 |
| -10.0 | 4.30 | 4.25 | 4.22 | 4.19 | 1.58 | 1.63 | 1.62 | 1.63 |
| -7.0 | 4.51 | 4.45 | 4.42 | 4.39 | 1.67 | 1.73 | 1.72 | 1.73 |
| -5.6 | 4.60 | 4.54 | 4.51 | 4.48 | 1.65 | 1.68 | 1.69 | 1.71 |
| -2.8 | 4.68 | 4.63 | 4.60 | 4.57 | 1.61 | 1.63 | 1.65 | 1.66 |
| 0.0 | 4.71 | 4.65 | 4.63 | 4.60 | 1.56 | 1.59 | 1.60 | 1.62 |
| 2.8 | 4.89 | 4.83 | 4.80 | 4.77 | 1.54 | 1.56 | 1.57 | 1.59 |
| 5.6 | 5.27 | 5.18 | 5.15 | 5.12 | 1.52 | 1.53 | 1.54 | 1.56 |
| 7.0 | 5.66 | 5.57 | 5.45 | 5.42 | 1.50 | 1.51 | 1.53 | 1.54 |
| 11.1 | 5.86 | 5.77 | 5.74 | 5.71 | 1.45 | 1.47 | 1.48 | 1.49 |
| 13.9 | 6.06 | 5.97 | 5.92 | 5.89 | 1.41 | 1.43 | 1.44 | 1.45 |
| 16.7 | 6.24 | 6.15 | 6.12 | 6.06 | 1.38 | 1.40 | 1.40 | 1.41 |
| 18.0 | 6.35 | 6.24 | 6.21 | 6.15 | 1.36 | 1.38 | 1.39 | 1.39 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS024D8S+38QUS024D8S | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 825 | -15.0 | 5.37 | 5.32 | 5.30 | 5.27 | 2.21 | 2.29 | 2.25 | 2.26 |
| -10.0 | 5.74 | 5.68 | 5.66 | 5.63 | 2.36 | 2.44 | 2.40 | 2.41 |
| -7.0 | 6.01 | 5.95 | 5.93 | 5.90 | 2.51 | 2.60 | 2.55 | 2.56 |
| -5.6 | 6.13 | 6.07 | 6.04 | 6.01 | 2.44 | 2.46 | 2.47 | 2.48 |
| -2.8 | 6.25 | 6.16 | 6.13 | 6.10 | 2.31 | 2.33 | 2.34 | 2.35 |
| 0.0 | 6.27 | 6.19 | 6.16 | 6.10 | 2.19 | 2.20 | 2.20 | 2.21 |
| 2.8 | 6.51 | 6.42 | 6.39 | 6.33 | 2.08 | 2.09 | 2.09 | 2.09 |
| 5.6 | 6.97 | 6.88 | 6.86 | 6.80 | 1.97 | 1.97 | 1.97 | 1.97 |
| 7.0 | 7.48 | 7.39 | 7.24 | 7.21 | 1.92 | 1.86 | 1.92 | 1.92 |
| 11.1 | 7.77 | 7.65 | 7.62 | 7.56 | 1.75 | 1.74 | 1.73 | 1.73 |
| 13.9 | 8.03 | 7.91 | 7.85 | 7.79 | 1.64 | 1.62 | 1.61 | 1.60 |
| 16.7 | 8.26 | 8.14 | 8.08 | 8.03 | 1.52 | 1.50 | 1.49 | 1.47 |
| 18.0 | 8.37 | 8.26 | 8.20 | 8.14 | 1.46 | 1.44 | 1.43 | 1.42 |
| 1035 | -15.0 | 5.48 | 5.43 | 5.40 | 5.38 | 2.24 | 2.32 | 2.27 | 2.27 |
| -10.0 | 5.85 | 5.80 | 5.77 | 5.74 | 2.39 | 2.47 | 2.42 | 2.43 |
| -7.0 | 6.13 | 6.07 | 6.05 | 6.02 | 2.54 | 2.62 | 2.57 | 2.58 |
| -5.6 | 6.25 | 6.19 | 6.16 | 6.13 | 2.47 | 2.49 | 2.50 | 2.51 |
| -2.8 | 6.36 | 6.27 | 6.25 | 6.22 | 2.34 | 2.35 | 2.36 | 2.37 |
| 0.0 | 6.39 | 6.30 | 6.27 | 6.22 | 2.21 | 2.22 | 2.23 | 2.23 |
| 2.8 | 6.65 | 6.56 | 6.51 | 6.48 | 2.10 | 2.11 | 2.11 | 2.11 |
| 5.6 | 7.12 | 7.03 | 6.97 | 6.94 | 2.00 | 2.00 | 1.99 | 1.99 |
| 7.0 | 7.63 | 7.53 | 7.39 | 7.36 | 1.94 | 1.88 | 1.94 | 1.94 |
| 11.1 | 7.91 | 7.82 | 7.77 | 7.71 | 1.77 | 1.76 | 1.75 | 1.75 |
| 13.9 | 8.17 | 8.05 | 8.00 | 7.94 | 1.65 | 1.64 | 1.63 | 1.62 |
| 16.7 | 8.43 | 8.32 | 8.26 | 8.17 | 1.54 | 1.51 | 1.50 | 1.49 |
| 18.0 | 8.55 | 8.43 | 8.37 | 8.29 | 1.48 | 1.45 | 1.44 | 1.43 |
| 1229 | -15.0 | 5.53 | 5.48 | 5.45 | 5.43 | 2.26 | 2.34 | 2.29 | 2.30 |
| -10.0 | 5.90 | 5.85 | 5.82 | 5.80 | 2.41 | 2.49 | 2.44 | 2.45 |
| -7.0 | 6.19 | 6.13 | 6.10 | 6.07 | 2.56 | 2.65 | 2.60 | 2.61 |
| -5.6 | 6.30 | 6.25 | 6.22 | 6.19 | 2.49 | 2.51 | 2.52 | 2.53 |
| -2.8 | 6.42 | 6.36 | 6.30 | 6.27 | 2.36 | 2.38 | 2.38 | 2.39 |
| 0.0 | 6.45 | 6.36 | 6.33 | 6.30 | 2.23 | 2.24 | 2.25 | 2.25 |
| 2.8 | 6.71 | 6.62 | 6.59 | 6.54 | 2.12 | 2.13 | 2.13 | 2.13 |
| 5.6 | 7.20 | 7.12 | 7.06 | 7.00 | 2.02 | 2.02 | 2.02 | 2.02 |
| 7.0 | 7.71 | 7.62 | 7.48 | 7.42 | 1.96 | 1.90 | 1.96 | 1.96 |
| 11.1 | 8.00 | 7.91 | 7.85 | 7.79 | 1.79 | 1.78 | 1.77 | 1.77 |
| 13.9 | 8.26 | 8.14 | 8.08 | 8.03 | 1.67 | 1.65 | 1.65 | 1.64 |
| 16.7 | 8.52 | 8.40 | 8.34 | 8.29 | 1.55 | 1.53 | 1.52 | 1.51 |
| 18.0 | 8.66 | 8.52 | 8.46 | 8.40 | 1.50 | 1.47 | 1.46 | 1.45 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS030D8S+38QUS030D8S | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1500 | -15.0 | 5.67 | 5.59 | 5.54 | 5.52 | 2.26 | 2.34 | 2.32 | 2.33 |
| -10.0 | 6.05 | 5.97 | 5.92 | 5.89 | 2.42 | 2.50 | 2.47 | 2.49 |
| -7.0 | 6.34 | 6.26 | 6.20 | 6.17 | 2.57 | 2.66 | 2.63 | 2.65 |
| -5.6 | 6.66 | 6.57 | 6.52 | 6.49 | 2.52 | 2.56 | 2.58 | 2.60 |
| -2.8 | 6.95 | 6.86 | 6.81 | 6.78 | 2.44 | 2.48 | 2.50 | 2.51 |
| 0.0 | 7.15 | 7.07 | 7.01 | 6.98 | 2.36 | 2.39 | 2.41 | 2.42 |
| 2.8 | 7.65 | 7.53 | 7.50 | 7.44 | 2.30 | 2.33 | 2.34 | 2.36 |
| 5.6 | 8.40 | 8.28 | 8.22 | 8.17 | 2.24 | 2.27 | 2.28 | 2.29 |
| 7.0 | 9.24 | 9.12 | 8.86 | 8.80 | 2.22 | 2.21 | 2.25 | 2.26 |
| 11.1 | 9.76 | 9.64 | 9.55 | 9.49 | 2.11 | 2.13 | 2.14 | 2.15 |
| 13.9 | 10.25 | 10.10 | 10.05 | 9.96 | 2.04 | 2.06 | 2.06 | 2.07 |
| 16.7 | 10.71 | 10.57 | 10.51 | 10.42 | 1.97 | 1.98 | 1.99 | 1.99 |
| 18.0 | 10.95 | 10.80 | 10.74 | 10.66 | 1.94 | 1.95 | 1.95 | 1.96 |
| 1800 | -15.0 | 5.78 | 5.70 | 5.68 | 5.65 | 2.29 | 2.36 | 2.34 | 2.36 |
| -10.0 | 6.17 | 6.09 | 6.06 | 6.04 | 2.44 | 2.52 | 2.50 | 2.52 |
| -7.0 | 6.46 | 6.38 | 6.35 | 6.33 | 2.60 | 2.68 | 2.66 | 2.68 |
| -5.6 | 6.78 | 6.69 | 6.66 | 6.63 | 2.55 | 2.59 | 2.61 | 2.63 |
| -2.8 | 7.10 | 7.01 | 6.95 | 6.92 | 2.47 | 2.50 | 2.52 | 2.54 |
| 0.0 | 7.30 | 7.21 | 7.15 | 7.10 | 2.38 | 2.41 | 2.43 | 2.45 |
| 2.8 | 7.79 | 7.67 | 7.65 | 7.59 | 2.32 | 2.35 | 2.37 | 2.38 |
| 5.6 | 8.57 | 8.46 | 8.40 | 8.34 | 2.26 | 2.29 | 2.30 | 2.31 |
| 7.0 | 9.42 | 9.29 | 9.03 | 8.97 | 2.24 | 2.23 | 2.27 | 2.28 |
| 11.1 | 9.93 | 9.81 | 9.76 | 9.67 | 2.13 | 2.15 | 2.16 | 2.17 |
| 13.9 | 10.42 | 10.31 | 10.22 | 10.16 | 2.06 | 2.07 | 2.08 | 2.09 |
| 16.7 | 10.92 | 10.77 | 10.71 | 10.63 | 1.99 | 2.00 | 2.01 | 2.01 |
| 18.0 | 11.18 | 11.00 | 10.95 | 10.86 | 1.95 | 1.96 | 1.97 | 1.97 |
| 2100 | -15.0 | 5.85 | 5.77 | 5.75 | 5.70 | 2.31 | 2.39 | 2.36 | 2.38 |
| -10.0 | 6.24 | 6.16 | 6.14 | 6.09 | 2.46 | 2.55 | 2.52 | 2.54 |
| -7.0 | 6.54 | 6.46 | 6.43 | 6.38 | 2.62 | 2.71 | 2.68 | 2.70 |
| -5.6 | 6.86 | 6.78 | 6.75 | 6.69 | 2.57 | 2.61 | 2.63 | 2.65 |
| -2.8 | 7.15 | 7.07 | 7.04 | 6.98 | 2.49 | 2.52 | 2.54 | 2.56 |
| 0.0 | 7.38 | 7.27 | 7.24 | 7.18 | 2.40 | 2.44 | 2.45 | 2.47 |
| 2.8 | 7.88 | 7.76 | 7.70 | 7.65 | 2.34 | 2.37 | 2.39 | 2.40 |
| 5.6 | 8.63 | 8.54 | 8.49 | 8.43 | 2.28 | 2.31 | 2.32 | 2.33 |
| 7.0 | 9.47 | 9.38 | 9.12 | 9.06 | 2.26 | 2.25 | 2.29 | 2.30 |
| 11.1 | 10.05 | 9.90 | 9.84 | 9.76 | 2.15 | 2.17 | 2.18 | 2.19 |
| 13.9 | 10.54 | 10.39 | 10.31 | 10.25 | 2.08 | 2.09 | 2.10 | 2.11 |
| 16.7 | 11.03 | 10.86 | 10.80 | 10.71 | 2.00 | 2.02 | 2.02 | 2.03 |
| 18.0 | 11.27 | 11.09 | 11.03 | 10.95 | 1.97 | 1.98 | 1.99 | 1.99 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS036D8S+38QUS036D8S | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1500 | -15.0 | 7.96 | 7.88 | 7.83 | 7.78 | 3.39 | 3.51 | 3.46 | 3.49 |
| -10.0 | 8.50 | 8.42 | 8.36 | 8.31 | 3.62 | 3.74 | 3.69 | 3.72 |
| -7.0 | 8.90 | 8.82 | 8.76 | 8.70 | 3.84 | 3.97 | 3.92 | 3.95 |
| -5.6 | 9.14 | 9.05 | 8.99 | 8.93 | 3.76 | 3.81 | 3.83 | 3.86 |
| -2.8 | 9.34 | 9.25 | 9.19 | 9.14 | 3.63 | 3.67 | 3.69 | 3.72 |
| 0.0 | 9.45 | 9.34 | 9.28 | 9.22 | 3.49 | 3.53 | 3.55 | 3.57 |
| 2.8 | 9.89 | 9.74 | 9.69 | 9.63 | 3.38 | 3.41 | 3.43 | 3.45 |
| 5.6 | 10.67 | 10.53 | 10.47 | 10.38 | 3.27 | 3.30 | 3.31 | 3.33 |
| 7.0 | 11.53 | 11.38 | 11.14 | 11.06 | 3.22 | 3.19 | 3.26 | 3.27 |
| 11.1 | 12.01 | 11.84 | 11.75 | 11.69 | 3.04 | 3.05 | 3.06 | 3.07 |
| 13.9 | 12.45 | 12.27 | 12.19 | 12.10 | 2.91 | 2.92 | 2.93 | 2.93 |
| 16.7 | 12.88 | 12.71 | 12.62 | 12.51 | 2.79 | 2.79 | 2.80 | 2.80 |
| 18.0 | 13.09 | 12.91 | 12.83 | 12.71 | 2.73 | 2.73 | 2.73 | 2.73 |
| 1800 | -15.0 | 8.13 | 8.05 | 8.00 | 7.95 | 3.43 | 3.54 | 3.50 | 3.52 |
| -10.0 | 8.68 | 8.60 | 8.55 | 8.49 | 3.66 | 3.78 | 3.73 | 3.76 |
| -7.0 | 9.09 | 9.01 | 8.95 | 8.90 | 3.88 | 4.01 | 3.96 | 3.99 |
| -5.6 | 9.34 | 9.25 | 9.19 | 9.14 | 3.80 | 3.85 | 3.87 | 3.90 |
| -2.8 | 9.54 | 9.45 | 9.40 | 9.34 | 3.66 | 3.71 | 3.73 | 3.75 |
| 0.0 | 9.66 | 9.54 | 9.45 | 9.40 | 3.52 | 3.56 | 3.58 | 3.60 |
| 2.8 | 10.09 | 9.95 | 9.89 | 9.83 | 3.41 | 3.45 | 3.46 | 3.48 |
| 5.6 | 10.88 | 10.73 | 10.67 | 10.61 | 3.30 | 3.33 | 3.34 | 3.36 |
| 7.0 | 11.76 | 11.61 | 11.38 | 11.29 | 3.25 | 3.22 | 3.29 | 3.30 |
| 11.1 | 12.25 | 12.07 | 12.01 | 11.93 | 3.07 | 3.08 | 3.09 | 3.10 |
| 13.9 | 12.68 | 12.51 | 12.42 | 12.33 | 2.94 | 2.95 | 2.95 | 2.96 |
| 16.7 | 13.15 | 12.94 | 12.86 | 12.77 | 2.81 | 2.82 | 2.82 | 2.82 |
| 18.0 | 13.35 | 13.17 | 13.06 | 12.97 | 2.75 | 2.75 | 2.76 | 2.76 |
| 2100 | -15.0 | 8.22 | 8.14 | 8.09 | 8.04 | 3.46 | 3.58 | 3.53 | 3.55 |
| -10.0 | 8.77 | 8.69 | 8.64 | 8.58 | 3.69 | 3.81 | 3.77 | 3.79 |
| -7.0 | 9.19 | 9.11 | 9.05 | 8.99 | 3.92 | 4.05 | 4.00 | 4.02 |
| -5.6 | 9.43 | 9.34 | 9.28 | 9.22 | 3.83 | 3.88 | 3.91 | 3.94 |
| -2.8 | 9.66 | 9.54 | 9.48 | 9.43 | 3.70 | 3.73 | 3.76 | 3.78 |
| 0.0 | 9.74 | 9.63 | 9.57 | 9.51 | 3.55 | 3.59 | 3.61 | 3.63 |
| 2.8 | 10.21 | 10.06 | 10.01 | 9.92 | 3.44 | 3.48 | 3.49 | 3.51 |
| 5.6 | 10.99 | 10.85 | 10.79 | 10.70 | 3.33 | 3.36 | 3.37 | 3.39 |
| 7.0 | 11.88 | 11.72 | 11.49 | 11.40 | 3.28 | 3.25 | 3.32 | 3.33 |
| 11.1 | 12.36 | 12.22 | 12.13 | 12.04 | 3.09 | 3.11 | 3.12 | 3.13 |
| 13.9 | 12.83 | 12.65 | 12.56 | 12.48 | 2.97 | 2.98 | 2.98 | 2.99 |
| 16.7 | 13.26 | 13.09 | 13.00 | 12.88 | 2.84 | 2.84 | 2.85 | 2.85 |
| 18.0 | 13.49 | 13.29 | 13.20 | 13.09 | 2.78 | 2.78 | 2.78 | 2.78 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS036D8S+38QUS042D8S | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1500 | -15.0 | 8.07 | 7.97 | 7.95 | 7.90 | 3.41 | 3.52 | 3.48 | 3.50 |
| -10.0 | 8.62 | 8.51 | 8.49 | 8.43 | 3.63 | 3.76 | 3.71 | 3.73 |
| -7.0 | 9.03 | 8.92 | 8.89 | 8.83 | 3.86 | 3.99 | 3.94 | 3.96 |
| -5.6 | 9.24 | 9.12 | 9.09 | 9.03 | 3.77 | 3.82 | 3.85 | 3.88 |
| -2.8 | 9.41 | 9.32 | 9.27 | 9.21 | 3.63 | 3.68 | 3.70 | 3.72 |
| 0.0 | 9.50 | 9.38 | 9.32 | 9.27 | 3.50 | 3.54 | 3.56 | 3.56 |
| 2.8 | 9.93 | 9.79 | 9.73 | 9.67 | 3.39 | 3.42 | 3.44 | 3.45 |
| 5.6 | 10.69 | 10.54 | 10.49 | 10.43 | 3.27 | 3.30 | 3.31 | 3.33 |
| 7.0 | 11.53 | 11.38 | 11.14 | 11.08 | 3.22 | 3.19 | 3.26 | 3.27 |
| 11.1 | 11.98 | 11.84 | 11.75 | 11.67 | 3.04 | 3.05 | 3.06 | 3.07 |
| 13.9 | 12.42 | 12.25 | 12.16 | 12.07 | 2.91 | 2.92 | 2.92 | 2.93 |
| 16.7 | 12.86 | 12.65 | 12.56 | 12.48 | 2.78 | 2.78 | 2.79 | 2.79 |
| 18.0 | 13.06 | 12.86 | 12.77 | 12.68 | 2.72 | 2.72 | 2.72 | 2.72 |
| 1800 | -15.0 | 8.21 | 8.13 | 8.08 | 8.03 | 3.44 | 3.56 | 3.51 | 3.53 |
| -10.0 | 8.76 | 8.68 | 8.63 | 8.58 | 3.67 | 3.79 | 3.75 | 3.77 |
| -7.0 | 9.18 | 9.10 | 9.04 | 8.98 | 3.90 | 4.03 | 3.98 | 4.00 |
| -5.6 | 9.41 | 9.32 | 9.27 | 9.21 | 3.81 | 3.86 | 3.89 | 3.91 |
| -2.8 | 9.61 | 9.50 | 9.44 | 9.38 | 3.67 | 3.71 | 3.73 | 3.76 |
| 0.0 | 9.70 | 9.59 | 9.53 | 9.47 | 3.53 | 3.56 | 3.58 | 3.60 |
| 2.8 | 10.14 | 9.99 | 9.93 | 9.88 | 3.42 | 3.45 | 3.47 | 3.48 |
| 5.6 | 10.92 | 10.78 | 10.69 | 10.63 | 3.31 | 3.33 | 3.35 | 3.36 |
| 7.0 | 11.76 | 11.61 | 11.38 | 11.29 | 3.26 | 3.22 | 3.29 | 3.30 |
| 11.1 | 12.25 | 12.07 | 11.98 | 11.90 | 3.06 | 3.08 | 3.09 | 3.09 |
| 13.9 | 12.68 | 12.51 | 12.42 | 12.33 | 2.94 | 2.94 | 2.95 | 2.95 |
| 16.7 | 13.12 | 12.91 | 12.83 | 12.74 | 2.81 | 2.81 | 2.81 | 2.81 |
| 18.0 | 13.32 | 13.12 | 13.03 | 12.94 | 2.74 | 2.74 | 2.74 | 2.74 |
| 2100 | -15.0 | 8.28 | 8.21 | 8.15 | 8.10 | 3.47 | 3.59 | 3.55 | 3.56 |
| -10.0 | 8.84 | 8.76 | 8.71 | 8.65 | 3.70 | 3.83 | 3.78 | 3.80 |
| -7.0 | 9.26 | 9.18 | 9.12 | 9.07 | 3.93 | 4.07 | 4.02 | 4.04 |
| -5.6 | 9.50 | 9.41 | 9.35 | 9.30 | 3.85 | 3.90 | 3.93 | 3.95 |
| -2.8 | 9.70 | 9.59 | 9.53 | 9.47 | 3.70 | 3.75 | 3.77 | 3.79 |
| 0.0 | 9.79 | 9.67 | 9.61 | 9.56 | 3.56 | 3.59 | 3.61 | 3.63 |
| 2.8 | 10.22 | 10.11 | 10.02 | 9.96 | 3.45 | 3.48 | 3.50 | 3.52 |
| 5.6 | 11.04 | 10.89 | 10.81 | 10.75 | 3.34 | 3.36 | 3.38 | 3.39 |
| 7.0 | 11.88 | 11.72 | 11.49 | 11.40 | 3.29 | 3.25 | 3.32 | 3.33 |
| 11.1 | 12.36 | 12.19 | 12.10 | 12.04 | 3.09 | 3.11 | 3.11 | 3.12 |
| 13.9 | 12.80 | 12.62 | 12.54 | 12.45 | 2.96 | 2.97 | 2.98 | 2.98 |
| 16.7 | 13.23 | 13.06 | 12.97 | 12.86 | 2.83 | 2.83 | 2.84 | 2.84 |
| 18.0 | 13.46 | 13.26 | 13.17 | 13.06 | 2.77 | 2.77 | 2.77 | 2.77 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS042D8S+38QUS036D8T | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1680 | -15.0 | 8.49 | 8.39 | 8.34 | 8.29 | 3.38 | 3.50 | 3.47 | 3.50 |
| -10.0 | 9.07 | 8.96 | 8.91 | 8.86 | 3.61 | 3.73 | 3.70 | 3.73 |
| -7.0 | 9.50 | 9.39 | 9.33 | 9.28 | 3.83 | 3.96 | 3.93 | 3.96 |
| -5.6 | 9.88 | 9.76 | 9.71 | 9.65 | 3.77 | 3.83 | 3.86 | 3.89 |
| -2.8 | 10.26 | 10.11 | 10.05 | 10.00 | 3.67 | 3.72 | 3.75 | 3.77 |
| 0.0 | 10.49 | 10.34 | 10.29 | 10.23 | 3.56 | 3.61 | 3.64 | 3.67 |
| 2.8 | 11.13 | 10.98 | 10.89 | 10.81 | 3.49 | 3.54 | 3.56 | 3.59 |
| 5.6 | 12.14 | 11.97 | 11.91 | 11.82 | 3.41 | 3.46 | 3.48 | 3.50 |
| 7.0 | 13.27 | 13.08 | 12.76 | 12.67 | 3.38 | 3.39 | 3.45 | 3.47 |
| 11.1 | 13.92 | 13.74 | 13.66 | 13.57 | 3.25 | 3.28 | 3.30 | 3.32 |
| 13.9 | 14.55 | 14.35 | 14.26 | 14.15 | 3.15 | 3.19 | 3.20 | 3.22 |
| 16.7 | 15.19 | 14.99 | 14.87 | 14.76 | 3.06 | 3.09 | 3.11 | 3.12 |
| 18.0 | 15.48 | 15.28 | 15.16 | 15.05 | 3.02 | 3.05 | 3.06 | 3.07 |
| 2040 | -15.0 | 8.65 | 8.55 | 8.50 | 8.45 | 3.42 | 3.53 | 3.51 | 3.53 |
| -10.0 | 9.24 | 9.13 | 9.08 | 9.03 | 3.65 | 3.77 | 3.74 | 3.77 |
| -7.0 | 9.68 | 9.57 | 9.51 | 9.46 | 3.87 | 4.00 | 3.97 | 4.00 |
| -5.6 | 10.08 | 9.97 | 9.91 | 9.85 | 3.81 | 3.87 | 3.90 | 3.93 |
| -2.8 | 10.46 | 10.32 | 10.26 | 10.20 | 3.71 | 3.75 | 3.78 | 3.81 |
| 0.0 | 10.69 | 10.55 | 10.49 | 10.40 | 3.59 | 3.65 | 3.68 | 3.70 |
| 2.8 | 11.33 | 11.18 | 11.10 | 11.04 | 3.52 | 3.57 | 3.59 | 3.62 |
| 5.6 | 12.37 | 12.23 | 12.14 | 12.05 | 3.44 | 3.49 | 3.51 | 3.53 |
| 7.0 | 13.49 | 13.34 | 12.99 | 12.90 | 3.41 | 3.42 | 3.48 | 3.50 |
| 11.1 | 14.21 | 14.00 | 13.92 | 13.83 | 3.27 | 3.31 | 3.33 | 3.35 |
| 13.9 | 14.84 | 14.64 | 14.55 | 14.44 | 3.18 | 3.21 | 3.23 | 3.25 |
| 16.7 | 15.48 | 15.28 | 15.16 | 15.08 | 3.09 | 3.12 | 3.13 | 3.14 |
| 18.0 | 15.80 | 15.57 | 15.48 | 15.37 | 3.04 | 3.07 | 3.08 | 3.10 |
| 2400 | -15.0 | 8.75 | 8.65 | 8.60 | 8.55 | 3.45 | 3.57 | 3.54 | 3.57 |
| -10.0 | 9.34 | 9.24 | 9.18 | 9.13 | 3.68 | 3.80 | 3.78 | 3.80 |
| -7.0 | 9.79 | 9.68 | 9.62 | 9.57 | 3.91 | 4.04 | 4.01 | 4.04 |
| -5.6 | 10.20 | 10.08 | 10.03 | 9.97 | 3.84 | 3.91 | 3.94 | 3.97 |
| -2.8 | 10.58 | 10.43 | 10.37 | 10.32 | 3.73 | 3.79 | 3.82 | 3.85 |
| 0.0 | 10.81 | 10.66 | 10.61 | 10.52 | 3.63 | 3.68 | 3.71 | 3.73 |
| 2.8 | 11.47 | 11.30 | 11.24 | 11.16 | 3.55 | 3.60 | 3.63 | 3.65 |
| 5.6 | 12.52 | 12.34 | 12.26 | 12.17 | 3.47 | 3.52 | 3.54 | 3.57 |
| 7.0 | 13.67 | 13.48 | 13.13 | 13.05 | 3.44 | 3.45 | 3.51 | 3.53 |
| 11.1 | 14.35 | 14.18 | 14.06 | 13.97 | 3.30 | 3.34 | 3.36 | 3.38 |
| 13.9 | 15.02 | 14.82 | 14.70 | 14.61 | 3.21 | 3.24 | 3.26 | 3.27 |
| 16.7 | 15.66 | 15.45 | 15.34 | 15.22 | 3.11 | 3.14 | 3.16 | 3.17 |
| 18.0 | 15.98 | 15.74 | 15.63 | 15.51 | 3.07 | 3.09 | 3.11 | 3.12 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS048D8S+38QUS048D8T | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1680 | -15.0 | 11.29 | 11.19 | 11.11 | 11.06 | 4.62 | 4.77 | 4.72 | 4.76 |
| -10.0 | 12.06 | 11.95 | 11.87 | 11.81 | 4.92 | 5.09 | 5.03 | 5.07 |
| -7.0 | 12.63 | 12.52 | 12.43 | 12.37 | 5.23 | 5.41 | 5.35 | 5.39 |
| -5.6 | 12.89 | 12.78 | 12.69 | 12.63 | 5.13 | 5.20 | 5.24 | 5.27 |
| -2.8 | 13.13 | 12.98 | 12.89 | 12.83 | 4.95 | 5.01 | 5.05 | 5.08 |
| 0.0 | 13.18 | 13.04 | 12.95 | 12.86 | 4.78 | 4.83 | 4.86 | 4.89 |
| 2.8 | 13.74 | 13.56 | 13.47 | 13.39 | 4.64 | 4.69 | 4.72 | 4.75 |
| 5.6 | 14.75 | 14.55 | 14.46 | 14.37 | 4.51 | 4.55 | 4.57 | 4.60 |
| 7.0 | 15.85 | 15.63 | 15.34 | 15.22 | 4.44 | 4.41 | 4.50 | 4.52 |
| 11.1 | 16.44 | 16.21 | 16.09 | 15.97 | 4.21 | 4.24 | 4.25 | 4.26 |
| 13.9 | 16.96 | 16.73 | 16.61 | 16.50 | 4.05 | 4.07 | 4.08 | 4.09 |
| 16.7 | 17.51 | 17.25 | 17.13 | 17.02 | 3.90 | 3.92 | 3.92 | 3.93 |
| 18.0 | 17.77 | 17.51 | 17.40 | 17.25 | 3.83 | 3.84 | 3.84 | 3.85 |
| 2040 | -15.0 | 11.52 | 11.42 | 11.34 | 11.29 | 4.67 | 4.82 | 4.76 | 4.80 |
| -10.0 | 12.30 | 12.19 | 12.11 | 12.06 | 4.98 | 5.14 | 5.08 | 5.12 |
| -7.0 | 12.89 | 12.77 | 12.69 | 12.63 | 5.29 | 5.47 | 5.40 | 5.44 |
| -5.6 | 13.15 | 13.04 | 12.95 | 12.89 | 5.18 | 5.26 | 5.29 | 5.33 |
| -2.8 | 13.39 | 13.24 | 13.15 | 13.10 | 5.00 | 5.07 | 5.10 | 5.13 |
| 0.0 | 13.47 | 13.30 | 13.21 | 13.13 | 4.82 | 4.88 | 4.90 | 4.93 |
| 2.8 | 14.03 | 13.85 | 13.74 | 13.65 | 4.69 | 4.74 | 4.77 | 4.78 |
| 5.6 | 15.04 | 14.87 | 14.75 | 14.66 | 4.55 | 4.59 | 4.62 | 4.64 |
| 7.0 | 16.13 | 15.95 | 15.66 | 15.54 | 4.48 | 4.45 | 4.54 | 4.56 |
| 11.1 | 16.76 | 16.55 | 16.44 | 16.32 | 4.24 | 4.27 | 4.29 | 4.30 |
| 13.9 | 17.31 | 17.08 | 16.96 | 16.84 | 4.08 | 4.10 | 4.12 | 4.13 |
| 16.7 | 17.86 | 17.60 | 17.48 | 17.37 | 3.93 | 3.95 | 3.95 | 3.96 |
| 18.0 | 18.12 | 17.86 | 17.74 | 17.60 | 3.86 | 3.87 | 3.87 | 3.88 |
| 2400 | -15.0 | 11.65 | 11.53 | 11.45 | 11.40 | 4.71 | 4.87 | 4.82 | 4.85 |
| -10.0 | 12.44 | 12.31 | 12.23 | 12.17 | 5.03 | 5.19 | 5.14 | 5.17 |
| -7.0 | 13.04 | 12.89 | 12.81 | 12.75 | 5.34 | 5.52 | 5.46 | 5.50 |
| -5.6 | 13.30 | 13.15 | 13.07 | 13.01 | 5.23 | 5.31 | 5.34 | 5.38 |
| -2.8 | 13.53 | 13.39 | 13.30 | 13.21 | 5.05 | 5.12 | 5.15 | 5.18 |
| 0.0 | 13.62 | 13.44 | 13.36 | 13.27 | 4.86 | 4.92 | 4.96 | 4.99 |
| 2.8 | 14.17 | 14.00 | 13.88 | 13.79 | 4.74 | 4.78 | 4.81 | 4.83 |
| 5.6 | 15.22 | 15.01 | 14.93 | 14.81 | 4.60 | 4.64 | 4.67 | 4.69 |
| 7.0 | 16.34 | 16.12 | 15.80 | 15.71 | 4.53 | 4.50 | 4.59 | 4.61 |
| 11.1 | 16.96 | 16.73 | 16.61 | 16.50 | 4.29 | 4.32 | 4.34 | 4.35 |
| 13.9 | 17.51 | 17.28 | 17.13 | 17.02 | 4.13 | 4.15 | 4.17 | 4.18 |
| 16.7 | 18.06 | 17.80 | 17.69 | 17.57 | 3.98 | 4.00 | 4.00 | 4.01 |
| 18.0 | 18.35 | 18.06 | 17.95 | 17.80 | 3.90 | 3.92 | 3.92 | 3.93 |

Note: The table shows the case where the operation frequency of a compressor is fixed.

**Specifications**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 42QSS060D8S+38QUS060D8T | | | | | | | | [SI\_Unit] | |
| INDOOR AIRFLOW (CMH) | HEATING PERFORMANCE AT INDOOR DRY BULB TEMPERATURE | | | | | | | | |
| OUTDOOR DB(°C) | TC:TOTAL CAPACITY IN KILOWATTS (KW) | | | | PI:TOTAL POWER IN KILOWATTS (KW) | | | |
| Indoor Conditions (DB °C ) | | | | Indoor Conditions (DB °C ) | | | |
| 16.0 | 20.0 | 22.0 | 24.0 | 16.0 | 20.0 | 22.0 | 24.0 |
| 1820 | -15.0 | 11.65 | 11.53 | 11.45 | 11.38 | 4.82 | 4.97 | 4.96 | 5.00 |
| -10.0 | 12.44 | 12.31 | 12.23 | 12.15 | 5.14 | 5.30 | 5.29 | 5.33 |
| -7.0 | 13.03 | 12.89 | 12.81 | 12.73 | 5.46 | 5.64 | 5.62 | 5.67 |
| -5.6 | 13.53 | 13.39 | 13.30 | 13.21 | 5.39 | 5.49 | 5.54 | 5.59 |
| -2.8 | 14.00 | 13.82 | 13.74 | 13.65 | 5.27 | 5.37 | 5.41 | 5.46 |
| 0.0 | 14.29 | 14.08 | 14.00 | 13.91 | 5.15 | 5.24 | 5.29 | 5.34 |
| 2.8 | 15.10 | 14.90 | 14.78 | 14.69 | 5.08 | 5.17 | 5.22 | 5.26 |
| 5.6 | 16.44 | 16.20 | 16.12 | 16.00 | 5.01 | 5.10 | 5.14 | 5.18 |
| 7.0 | 17.90 | 17.65 | 17.21 | 17.10 | 4.99 | 5.05 | 5.12 | 5.16 |
| 11.1 | 18.75 | 18.52 | 18.37 | 18.26 | 4.85 | 4.93 | 4.97 | 5.01 |
| 13.9 | 19.56 | 19.30 | 19.19 | 19.04 | 4.76 | 4.83 | 4.87 | 4.91 |
| 16.7 | 20.38 | 20.12 | 19.97 | 19.83 | 4.67 | 4.74 | 4.77 | 4.80 |
| 18.0 | 20.78 | 20.49 | 20.35 | 20.20 | 4.63 | 4.69 | 4.72 | 4.76 |
| 2210 | -15.0 | 11.88 | 11.75 | 11.68 | 11.60 | 4.86 | 5.02 | 5.00 | 5.04 |
| -10.0 | 12.69 | 12.55 | 12.47 | 12.39 | 5.18 | 5.36 | 5.33 | 5.38 |
| -7.0 | 13.29 | 13.15 | 13.07 | 12.98 | 5.51 | 5.69 | 5.67 | 5.72 |
| -5.6 | 13.79 | 13.65 | 13.56 | 13.47 | 5.44 | 5.54 | 5.59 | 5.64 |
| -2.8 | 14.26 | 14.08 | 14.00 | 13.91 | 5.32 | 5.42 | 5.47 | 5.52 |
| 0.0 | 14.55 | 14.37 | 14.29 | 14.17 | 5.20 | 5.29 | 5.34 | 5.39 |
| 2.8 | 15.39 | 15.19 | 15.07 | 14.98 | 5.13 | 5.22 | 5.27 | 5.31 |
| 5.6 | 16.76 | 16.52 | 16.44 | 16.32 | 5.06 | 5.15 | 5.19 | 5.24 |
| 7.0 | 18.25 | 18.00 | 17.56 | 17.45 | 5.04 | 5.10 | 5.17 | 5.21 |
| 11.1 | 19.13 | 18.87 | 18.75 | 18.64 | 4.90 | 4.98 | 5.02 | 5.06 |
| 13.9 | 19.97 | 19.68 | 19.56 | 19.42 | 4.81 | 4.88 | 4.92 | 4.95 |
| 16.7 | 20.78 | 20.49 | 20.35 | 20.20 | 4.72 | 4.78 | 4.82 | 4.85 |
| 18.0 | 21.19 | 20.90 | 20.75 | 20.61 | 4.67 | 4.74 | 4.77 | 4.80 |
| 2600 | -15.0 | 12.01 | 11.86 | 11.79 | 11.74 | 4.91 | 5.07 | 5.05 | 5.10 |
| -10.0 | 12.83 | 12.67 | 12.59 | 12.53 | 5.24 | 5.41 | 5.39 | 5.44 |
| -7.0 | 13.44 | 13.27 | 13.19 | 13.13 | 5.57 | 5.75 | 5.73 | 5.77 |
| -5.6 | 13.94 | 13.76 | 13.68 | 13.62 | 5.49 | 5.60 | 5.65 | 5.70 |
| -2.8 | 14.40 | 14.23 | 14.14 | 14.06 | 5.37 | 5.47 | 5.52 | 5.57 |
| 0.0 | 14.69 | 14.52 | 14.40 | 14.32 | 5.25 | 5.35 | 5.39 | 5.44 |
| 2.8 | 15.54 | 15.33 | 15.22 | 15.13 | 5.18 | 5.27 | 5.32 | 5.36 |
| 5.6 | 16.93 | 16.70 | 16.58 | 16.47 | 5.11 | 5.20 | 5.24 | 5.29 |
| 7.0 | 18.42 | 18.17 | 17.74 | 17.62 | 5.09 | 5.15 | 5.22 | 5.26 |
| 11.1 | 19.30 | 19.07 | 18.93 | 18.81 | 4.95 | 5.03 | 5.07 | 5.11 |
| 13.9 | 20.15 | 19.88 | 19.74 | 19.62 | 4.86 | 4.93 | 4.97 | 5.00 |
| 16.7 | 20.99 | 20.70 | 20.55 | 20.41 | 4.76 | 4.83 | 4.87 | 4.90 |
| 18.0 | 21.39 | 21.10 | 20.96 | 20.81 | 4.72 | 4.78 | 4.82 | 4.85 |

Note: The table shows the case where the operation frequency of a compressor is fixed.