## Efficiency Class
France |  | A ++ (remplacement uniquement) | A+++ (remplacement et primo installation)
| Puissance climatiseurs en kW | 6,1<= SEER* < 8,5 | SEER* => 8,5
| 2,05 ≤ P < 2,64 | 150 | 300
| 2,64 ≤ P < 3,52 | 170 | 350
| 3,52 ≤ P < 4,40 | 220 | 450
| 4,40 ≤ P < 5,28 | 290 | 590
| 5,28 ≤ P < 6,16 | 340 | 700
| 6,16 ≤ P < 7,03 | 390 | 800
| 7,03 ≤ P < 8,24 | 440 | 900
| 8,24 ≤ P < 8,78 | 540 | 1 000 €

## 12K
Specification of LC(R410A) 12K
SYSTEM |  | Cassette 12K | Console 12K | A6 Ducted 12K
Cooling capacity | kW | 3.52 (1.4~3.9) | 3.52 (1.0~3.5) | 3.52 (0.5~3.8)
Heating capacity | kW | 4.00 (1.2~4.2) | 3.70 (1.0~4.0) | 3.80 (1.0~4.0)
Heating capacity at -7℃ | kW | 2.7 | 2.8 | 2.7
Heating capacity at -10℃ | kW | 2.7 | 2.6 | 2.3
Heating capacity at -15℃ | kW | 2.4 | 2.4 | 2
P design capacity cooling | kW | 3.52 | 3.52 | 3.52
P design capacity heating(average) | kW | 2.94 | 2.91 | 2.6
P design capacity heating(warmer) | kW | 3.5 | 3.6 | 3.3
SEER / SCOP(average) / SCOP(warmer) | W/W | 6.2 / 4.1 / 5.1 | 5.9 / 4.0 / 4.7 | 5.6 / 4.0 / 4.8
Energy label |  | A++ / A+ / A+++ | A+ / A+ / A++ | A+ / A+ / A++
Yearly energy consumption | kWh | 199/1002/960 | 207/1016/1072 | 220 / 910 / 963
EER/COP | W/W | 3.1/3.6 | 3.0/3.5 | 2.69 / 3.19
Standard current (cooling) | A | 5 | 5 | 5.8
Standard input (cooling) | W | 1140 | 1140 | 1310
Standard current (heating) | A | 4.7 | 4.7 | 5.3
Standard input (heating) | W | 1080 | 1060 | 1190
OUTDOOR UNIT |  | 38QUS012DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 10
Rated input | W | 2300
Refrigerant amount | kg | 1.05 | 0.65
Compressor model |  | ASN98D22UFZ
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 370
Liquid side/ Gas side | mm(inch) | Φ6.35/Φ9.52 (1/4"/3/8") | Φ6.35/Φ9.52 (1/4"/3/8")
Standard piping length | m | 5 | 5
Min piping length | m | 3 | 3
Max piping length | m | 25 | 20
Max difference | m | 10 | 8
Additional charge | g/m | 15 | 15
Sound power level | dB(A) | 65
Sound pressure level | dB(A) | 56
Airflow | m3/h | 2100
Weight (Net/Gross) | kg | 28.5 / 31.5
Dimensions (WxDxH) | mm | 800×333×554
Packing (WxDxH) | mm | 920×390×625
INDOOR UNIT |  | 42QTD012D8S | 42QZA012D8S | 42QSS012D8S
Indoor fan motor input | W | 45 | 66.6 | 130
Indoor fan motor max current | A | 0.4 | 0.6 | 1.11
Sound power level | dB(A) | 59 | 60 | 60
Sound pressure level (high/med/low) | dB(A) | 42/39/36 | 43/41/35 | 42 / 36 / 30
Air flow (high/med/low) | m3/h | 560/430/390 | 530/480/360 | 580 / 480 / 300
External static pressure | Pa | 0 | 0 | 0~30
Weight (Net/Gross)(Body) | kg | 16.5/19.0 | 15.0/19.5 | 18.0 / 22.0
Weight (Net/Gross)(Panel) | kg | 2.5/4.5 | / | /
Dimensions (WxDxH)(Body) | mm | 570x570x260 | 700x600x210 | 700×450×200
Packing (WxDxH)(Body) | mm | 662x662x317 | 810x710x310 | 860×540×285
Dimensions (WxDxH)(Panel) | mm | 647x647x50 | / | /
Packing (WxDxH)(Panel) | mm | 715x715x123 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 18K
Specification of LC(R410A) 18K
SYSTEM |  | Cassette 18K(New) | Under-ceiling 18K(New) | Ducted 18K(New)
Cooling capacity | kW | 5.20 (2.90~5.74) | 5.30 (2.86~5.61) | 5.30 (2.55~5.35)
Heating capacity | kW | 5.57 (2.37~6.29) | 5.57 (2.40~5.83) | 5.28 (2.20~6.15)
Heating capacity at -7℃ | kW | 3.9 | 4.3 | 4
Heating capacity at -10℃ | kW | 3.9 | 3.9 | 3.6
Heating capacity at -15℃ | kW | 2.2 | 3.2 | 2.5
P design capacity cooling | kW | 5.2 | 5.3 | 5.3
P design capacity heating(average) | kW | 4.6 | 4.4 | 4.3
P design capacity heating(warmer) | kW | 4.9 | 4.8 | 4.5
SEER / SCOP(average) / SCOP(warmer) | W/W | 6.1 / 4.0 / 5.2 | 6.1 / 4.0 / 5.1 | 6.1 / 4.0 / 5.0
Energy label |  | A++ / A+ / A+++ | A++ / A+ / A+++ | A++ / A+ / A++
Yearly energy consumption | kWh | 298/1610/1319 | 304/1554/1318 | 304/1523/1258
EER/COP | W/W | 3.06/3.91 | 3.25/3.71 | 3.24/3.72
Standard current (cooling) | A | 7.5 | 7.3 | 7.2
Standard input (cooling) | W | 1700 | 1630 | 1635
Standard current (heating) | A | 6.3 | 6.6 | 6.3
Standard input (heating) | W | 1425 | 1500 | 1420
OUTDOOR UNIT |  | 38QUS018DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 13.5
Rated input | W | 2950
Refrigerant amount | kg | 1.35
Compressor model |  | KSN140D21UFZ
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 440
Liquid side/ Gas side | mm(inch) | Φ6.35/Φ12.7 (1/4"/1/2")
Standard piping length | m | 5
Min piping length | m | 3
Max piping length | m | 30
Max difference | m | 20
Additional charge | g/m | 15
Sound power level | dB(A) | 65 |  |  | Ceiling:64/Cassette:64/Ducted:63
Sound pressure level | dB(A) | 57 |  |  | Ceiling:61/Cassette:55.5/Ducted:54.5
Airflow | m3/h | 2000
Weight (Net/Gross) | kg | 34.5/37.0
Dimensions (WxDxH) | mm | 800×333×554
Packing (WxDxH) | mm | 920×390×625
INDOOR UNIT |  | 42QTD018D8S-1(New) | 42QZL018D8S-1(New) | 42QSS018D8S
Indoor fan motor input | W | 45 | 96 | 90
Indoor fan motor max current | A | 0.4 | 0.94 | 1.2
Sound power level | dB(A) | 60 | 61 | 61
Sound pressure level (high/med/low) | dB(A) | 45/42/36 | 44/42/36 | 45/38/33
Air flow (high/med/low) | m3/h | 680/550/400 | 880/760/650 | 880/650/350
External static pressure | Pa | 0 | 0 | 0~100
Weight (Net/Gross)(Body) | kg | 16.5/19.5 | 28.0/33.5 | 24.5/29.5
Weight (Net/Gross)(Panel) | kg | 2.5/4.5 | / | /
Dimensions (WxDxH)(Body) | mm | 570x570x260 | 1068x675x235 | 880x674x210
Packing (WxDxH)(Body) | mm | 662x662x317 | 1145x755x318 | 1070x725x280
Dimensions (WxDxH)(Panel) | mm | 647x647x50 | / | /
Packing (WxDxH)(Panel) | mm | 715x715x123 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 24K
Specification of LC(R410A) 24K
SYSTEM |  | Cassette 24K | Under-ceiling 24K | Ducted 24K
Cooling capacity | kW | 7.03 (2.5~8.0) | 7.03 (2.5~8.0) | 7.03 (2.5~7.7)
Heating capacity | kW | 7.03 (2.5~8.5) | 7.30 (2.5~8.5) | 7.40 (2.4~8.7)
Heating capacity at -7℃ | kW | 5.4 | 5.3 | 5.3
Heating capacity at -10℃ | kW | 5 | 5.5 | 4.7
Heating capacity at -15℃ | kW | 3.7 | 4.9 | 3.5
P design capacity cooling | kW | 7.03 | 7.03 | 7.03
P design capacity heating(average) | kW | 5.54 | 5.2 | 5.2
P design capacity heating(warmer) | kW | 7.8 | 7.8 | 7.5
SEER / SCOP(average) / SCOP(warmer) | W/W | 6.1 / 4.0 / 4.8 | 5.8 / 4.0 / 4.6 | 6.1 / 4.0 / 5.1
Energy label |  | A++ / A+ / A++ | A+ / A+ / A++ | A++ / A+ / A+++
Yearly energy consumption | kWh | 403/1937/2277 | 424/1820/2373 | 401/1820/2058
EER/COP | W/W | 3.0/3.2 | 2.9/3.3 | 3.1/3.4
Standard current (cooling) | A | 10.5 | 11 | 9.7
Standard input (cooling) | W | 2400 | 2430 | 2300
Standard current (heating) | A | 9.6 | 9.6 | 9.5
Standard input (heating) | W | 2180 | 2180 | 2150
OUTDOOR UNIT |  | 38QUS024DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 16
Rated input | W | 3680
Refrigerant amount | kg | 2.05 | 2 | 2
Compressor model |  | ATF235D22UMT
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 670
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9(3/8"/5/8") | Φ9.52/Φ15.9(3/8"/5/8") | Φ9.52/Φ15.9(3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 50 | 20 | 20
Max difference | m | 25 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 69
Sound pressure level | dB(A) | 61
Airflow | m3/h | 2700
Weight (Net/Gross) | kg | 50/54.5
Dimensions (WxDxH) | mm | 845×363×702
Packing (WxDxH) | mm | 965×395×775
INDOOR UNIT |  | 42QTD024DS-1 | 42QZL024DS-1 | 42QSS024DS-1
Indoor fan motor input | W | 141 | 100 | 90
Indoor fan motor max current | A | 0.8 | 1.11 | 1.2
Sound power level | dB(A) | 61 | 65 | 61
Sound pressure level (high/med/low) | dB(A) | 49/46/43 | 50/47/41 | 43/40/38
Air flow (high/med/low) | m3/h | 1350/1200/1070 | 1150/1040/790 | 1120/900/420
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 24.5/30.0 | 27.0/32.0 | 30.2/37.3
Weight (Net/Gross)(Panel) | kg | 5 / 8 | / | /
Dimensions (WxDxH)(Body) | mm | 840x840x245 | 1068x675x235 | 1100x774x249
Packing (WxDxH)(Body) | mm | 900x900x265 | 1145x755x318 | 1305x805x315
Dimensions (WxDxH)(Panel) | mm | 950x950x55 | / | /
Packing (WxDxH)(Panel) | mm | 1035x1035x90 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 30K
Specification of LC(R410A) 30K
SYSTEM |  | Cassette 30K | Under-ceiling 30K | Ducted 30K
Cooling capacity | kW | 8.40 (2.1~10.5) | 8.40 (2.1~10.5) | 8.70 (2.1~10.5)
Heating capacity | kW | 9.10 (2.1~10.5) | 9.00 (2.1~10.8) | 9.30 (2.1~10.8)
Heating capacity at -7℃ | kW | 6.6 | 6.5 | 7
Heating capacity at -10℃ | kW | 6.1 | 6.2 | 6.6
Heating capacity at -15℃ | kW | 5.5 | 5.7 | 6
P design capacity cooling | kW | 8.4 | 8.4 | 8.7
P design capacity heating(average) | kW | 7 | 7.91 | 7.23
P design capacity heating(warmer) | kW | 7.2 | 7.8 | 7
SEER/SCOP(average)/SCOP(warmer) | W/W | 6.4 / 4.0 / 5.2 | 6.3 / 4.0 / 5.2 | 6.5 / 4.0 / 4.8
Energy label |  | A++ / A+ / A+++ | A++ / A+ / A+++ | A++ / A+ / A++
Yearly energy consumption | kWh | 459/2453/1950 | 469/2769/2108 | 469/2532/2040
EER/COP | W/W | 3.0/3.8 | 2.8/3.6 | 3.0/3.7
Standard current (cooling) | A | 12.4 | 13.5 | 13.1
Standard input (cooling) | W | 2780 | 2970 | 2860
Standard current (heating) | A | 10.6 | 11.3 | 11.6
Standard input (heating) | W | 2300 | 2480 | 2490
OUTDOOR UNIT |  | 38QUS030DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 19
Rated input | W | 3400
Refrigerant amount | kg | 2.8
Compressor model |  | ATF235D22UMT
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 670
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 50 | 20 | 20
Max difference | m | 25 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 70
Sound pressure level | dB(A) | 62
Airflow | m3/h | 4300
Weight (Net/Gross) | kg | 62.9/68.5
Dimensions (WxDxH) | mm | 946x410x810
Packing (WxDxH) | mm | 1090x500x885
INDOOR UNIT |  | 42QTD030DS-1 | 42QZL030DS-1 | 42QSS030DS-1
Indoor fan motor input | W | 141 | 130 | 250
Indoor fan motor max current | A | 0.8 | 1.36 | 1.52
Sound power level | dB(A) | 65 | 65 | 65
Sound pressure level (high/med/low) | dB(A) | 50/48/44 | 54/49/44 | 47/45/42
Air flow (high/med/low) | m3/h | 1390/1110/750 | 1650/1450/1250 | 1900/1560/1205
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 26.5/30.5 | 31/36.5 | 40.5/48.5
Weight (Net/Gross)(Panel) | kg | 5 / 8 | / | /
Dimensions (WxDxH)(Body) | mm | 840x840x245 | 1285x675x235 | 1360x774x249
Packing (WxDxH)(Body) | mm | 900x900x265 | 1360x755x318 | 1570x805x315
Dimensions (WxDxH)(Panel) | mm | 950x950x55 | / | /
Packing (WxDxH)(Panel) | mm | 1035x1035x90 | / | /
Note
* Sound data @ cooling mode
* -7℃/-10℃/-15℃ heating @ free frequency

## 36K(1Ph)
Specification of LC 36K(R410A) (single phase)
SYSTEM |  | Cassette 36K | Under-ceiling 36K | Ducted 36K
Cooling capacity | kW | 10.2 (4.5~11.0) | 10.4 (4.4~11.0) | 10.2 (3.7~11.0)
Heating capacity | kW | 11.3 (3.7~13.7) | 11.9 (3.7~13.8) | 12.7 (3.0~14.0)
Heating capacity at -7℃ | kW | 9.7 | 9.8 | 10.3
Heating capacity at -10℃ | kW | 8.3 | 8.4 | 9.6
Heating capacity at -15℃ | kW | 8.2 | 8.2 | 8.3
P design capacity cooling | kW | 10.2 | 10.4 | 10.2
P design capacity heating(average) | kW | 9.3 | 10.2 | 9.9
P design capacity heating(warmer) | kW | 10.3 | 10.6 | 10.6
SEER/SCOP(average)/SCOP(warmer) | W/W | 6.0 / 4.0 / 5.0 | 6.3 / 4.0 / 5.1 | 6.2 / 4.0 / 5.1
Energy label |  | A+ / A+ / A++ | A++ / A+ / A+++ | A++ / A+ / A+++
Yearly energy consumption | kWh | 588/3244/2894 | 576/3561/2922 | 576/3465/2910
EER/COP | W/W | 2.7/3.4 | 2.6/3.7 | 2.6/3.7
Standard current (cooling) | A | 16.6 | 17.1 | 17.4
Standard input (cooling) | W | 3750 | 3970 | 3890
Standard current (heating) | A | 15.2 | 14 | 15.7
Standard input (heating) | W | 3300 | 3200 | 3410
OUTDOOR UNIT |  | 38QUS036DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 23
Rated input | W | 4800
Refrigerant amount | kg | 3.65 | 3.2 | 3.2
Compressor model |  | ATF310D43UMT
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 1000
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 65 | 20 | 20
Max difference | m | 30 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 70
Sound pressure level | dB(A) | 64
Airflow | m3/h | 4150
Weight (Net/Gross) | kg | 70.5/76.1 | 67.2/72.9 | 67.2/72.9
Dimensions (WxDxH) | mm | 946x410x810
Packing (WxDxH) | mm | 1090x500x885
INDOOR UNIT |  | 42QTD036R8S | 42QZL036R8S | 42QSS036R8S
Indoor fan motor input | W | 141 | 96*2 | 250
Indoor fan motor max current | A | 0.8 | 1.15*2 | 1.52
Sound power level | dB(A) | 65 | 65 | 65
Sound pressure level (high/med/low) | dB(A) | 51/49/46 | 50/46/42 | 45/42/39
Air flow (high/med/low) | m3/h | 1770/1620/1440 | 2160/1840/1430 | 1400/1150/750
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 27.5/31.0 | 41.5/48.0 | 40.5/48.5
Weight (Net/Gross)(Panel) | kg | 6.0/9.0 | / | /
Dimensions (WxDxH)(Body) | mm | 840x840x245 | 1650x675x235 | 1360x774x249
Packing (WxDxH)(Body) | mm | 900x900x265 | 1725x755x318 | 1570x805x315
Dimensions (WxDxH)(Panel) | mm | 950x950x55 | / | /
Packing (WxDxH)(Panel) | mm | 1035x1035x90 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 36K(3Ph)
Specification of LC 36K(R410A) (3 phase)
SYSTEM |  | Cassette 36K(New) | Under-ceiling 36K(New) | Ducted 36K(New)
Cooling capacity | kW | 10.50 (2.93~12.02) | 10.50 (2.93~12.02) | 10.30 (2.40~12.01)
Heating capacity | kW | 11.13 (2.64~13.19) | 11.13 (2.64~13.19) | 11.14 (2.78~13.20)
Heating capacity at -7℃ | kW | 9.6 | 9.7 | 9.9
Heating capacity at -10℃ | kW | 8.2 | 8.3 | 9.1
Heating capacity at -15℃ | kW | 8.1 | 8.2 | 8.1
P design capacity cooling | kW | 10.5 | 10.5 | 10.3
P design capacity heating(average) | kW | 10.1 | 10.3 | 10.5
P design capacity heating(warmer) | kW | 10.5 | 10.5 | 10.5
SEER/SCOP(average)/SCOP(warmer) | W/W | 6.1 / 4.0 / 5.1 | 6.1 / 4.0 / 5.1 | 6.1 / 4.0 / 5.1
Energy label |  | A++ / A+ / A+++ | A++ / A+ / A+++ | A++ / A+ / A+++
Yearly energy consumption | kWh | 602/3710/2882 | 602/3605/2882 | 606/3675/2882
EER/COP | W/W | 2.59/3.61 | 2.59/3.73 | 2.54/3.61
Standard current (cooling) | A | 7 | 7 | 7.48
Standard input (cooling) | W | 4060 | 4060 | 4060
Standard current (heating) | A | 5.3 | 5.2 | 5.7
Standard input (heating) | W | 3085 | 2985 | 3085
OUTDOOR UNIT |  | 38QUS036DT-2
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 380~415V / 50Hz / 3Ph
Rated current | A | 10
Rated input | W | 5600
Refrigerant amount | kg | 3.2
Compressor model |  | ATF310D43UMT
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 1000
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 65 | 20 | 20
Max difference | m | 30 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 70
Sound pressure level | dB(A) | 64
Airflow | m3/h | 3800
Weight (Net/Gross) | kg | 81.0/87.0
Dimensions (WxDxH) | mm | 946x410x810 | 946x410x810 | 946x410x810
Packing (WxDxH) | mm | 1090x500x885 | 1090x500x875 | 1090x500x875
INDOOR UNIT |  | 42QTD036R8S | 42QZL036R8S | 42QSS036R8S
Indoor fan motor input | W | 141 | 96*2 | 250
Indoor fan motor max current | A | 0.8 | 1.15*2 | 1.52
Sound power level | dB(A) | 65 | 65 | 65
Sound pressure level (high/med/low) | dB(A) | 51/49/46 | 50/46/42 | 45/42/39
Air flow (high/med/low) | m3/h | 1770/1620/1440 | 2160/1840/1430 | 1400/1150/750
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 27.5/31.0 | 41.5/48.0 | 40.5/48.5
Weight (Net/Gross)(Panel) | kg | 6.0/9.0 | / | /
Dimensions (WxDxH)(Body) | mm | 840x840x245 | 1650x675x235 | 1360x774x249
Packing (WxDxH)(Body) | mm | 900x900x265 | 1725x755x318 | 1570x805x315
Dimensions (WxDxH)(Panel) | mm | 950x950x55 | / | /
Packing (WxDxH)(Panel) | mm | 1035x1035x90 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 48K(1Ph)
Specification of LC 48K(R410A) (single phase)
SYSTEM |  | Cassette 48K | Under-ceiling 48K | Ducted 48K
Cooling capacity | kW | 13.4 (4.8~14.0) | 13.6 (4.8~14.0) | 13.7 (5.1~14.4)
Heating capacity | kW | 15.5 (5.4~16.0) | 15.5 (5.4~16.0) | 15.4 (4.4~16.4)
Heating capacity at -7℃ | kW | 10.4 | 11.3 | 10.8
Heating capacity at -10℃ | kW | 9.9 | 10.8 | 10.3
Heating capacity at -15℃ | kW | 8.4 | 9.4 | 8.9
P design capacity cooling | kW | 13.4 | 13.6 | 13.7
P design capacity heating(average) | kW | 10.7 | 10.6 | 10.3
P design capacity heating(warmer) | kW | 11.8 | 11.9 | 11.6
SEER/SCOP(average)/SCOP(warmer) | W/W | 5.5 / 4.0 / 5.0 | 5.9 / 4.0 / 5.3 | 5.8 / 4.0 / 4.9
Energy label |  | A / A+ / A++ | A+ / A+ / A+++ | A+ / A+ / A++
Yearly energy consumption | kWh | 852/3756/3323 | 810/3718/3167 | 826/3597/3337
EER/COP | W/W | 2.4/2.9 | 2.4/2.9 | 2.7/3.5
Standard current (cooling) | A | 24.1 | 24.4 | 22.3
Standard input (cooling) | W | 5530 | 5620 | 5070
Standard current (heating) | A | 23.1 | 23.4 | 19.5
Standard input (heating) | W | 5300 | 5300 | 4400
OUTDOOR UNIT |  | 38QUS048DS-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 220-240V / 50Hz / 1Ph
Rated current | A | 26.5
Rated input | W | 6100
Refrigerant amount | kg | 4
Compressor model |  | ATQ420D1UMU
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 1400
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 65 | 20 | 20
Max difference | m | 30 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 75
Sound pressure level | dB(A) | 64
Airflow | m3/h | 6800
Weight (Net/Gross) | kg | 95.1/108.4
Dimensions (WxDxH) | mm | 952x415x1333 | 952x415x1333 | 952x415x1333
Packing (WxDxH) | mm | 1095x495x1480 | 1095x495x1480 | 1095x495x1480
INDOOR UNIT |  | 42QTD048R8S | 42QZL048R8S | 42QSS048R8S
Indoor fan motor input | W | 141 | 96*2 | 560
Indoor fan motor max current | A | 0.45 | 0.85*2 | 4.1
Sound power level | dB(A) | 67 | 69 | 71
Sound pressure level (high/med/low) | dB(A) | 52/50/49 | 54/50/46 | 51/50/48
Air flow (high/med/low) | m3/h | 1720 / 1570 / 1380 | 2330 / 1930 / 1420 | 2400 / 2040 / 1680
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 29.0 / 33.0 | 41.2 / 47.6 | 47.5 / 56.0
Weight (Net/Gross)(Panel) | kg | 6.0 / 9.0 | / | /
Dimensions (WxDxH)(Body) | mm | 840×840×287 | 1650x675x235 | 1200x874x300
Packing (WxDxH)(Body) | mm | 900×900×307 | 1725x755x318 | 1405x915x365
Dimensions (WxDxH)(Panel) | mm | 950×950×55 | / | /
Packing (WxDxH)(Panel) | mm | 1035×1035×90 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 48K(3Ph)
Specification of LC 48K(R410A) (3 phase)
SYSTEM |  | Cassette 48K | Under-ceiling 48K | Ducted 48K
Cooling capacity | kW | 13.4 (4.8~14.0) | 13.6 (4.8~14.0) | 13.7 (4.9~14.2)
Heating capacity | kW | 15.5 (5.4~16.0) | 15.5 (5.4~16.0) | 15.4 (4.7~16.9)
Heating capacity at -7℃ | kW | 10.5 | 11.1 | 11.6
Heating capacity at -10℃ | kW | 10 | 10.5 | 10.7
Heating capacity at -15℃ | kW | 8.5 | 8.6 | 9.1
P design capacity cooling | kW | 13.4 | 13.6 | 13.7
P design capacity heating(average) | kW | 11 | 11.3 | 11.5
P design capacity heating(warmer) | kW | 11.8 | 12.1 | 12.4
SEER/SCOP(average)/SCOP(warmer) | W/W | 5.6 / 4.0 / 5.1 | 5.8 / 4.0 / 5.3 | 5.9 / 4.0 / 5.4
Energy label |  | A+ / A+ / A+++ | A+ / A+ / A+++ | A+ / A+ / A+++
Yearly energy consumption | kWh | 834/3847/3231 | 815/3954/3179 | 813/4030/3206
EER/COP | W/W | 2.5/3.0 | 2.4/3.0 | 2.6/3.7
Standard current (cooling) | A | 8.9 | 9.3 | 8.4
Standard input (cooling) | W | 5310 | 5620 | 5230
Standard current (heating) | A | 8.5 | 8.6 | 6.9
Standard input (heating) | W | 5130 | 5130 | 4240
OUTDOOR UNIT |  | 38QUS048DT-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 380~415V / 50Hz / 3Ph
Rated current | A | 13
Rated input | W | 6100
Refrigerant amount | kg | 4
Compressor model |  | ATQ420D1UMU
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 1400
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 65 | 20 | 20
Max difference | m | 30 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 75
Sound pressure level | dB(A) | 64
Airflow | m3/h | 6800
Weight (Net/Gross) | kg | 108.1/121.2
Dimensions (WxDxH) | mm | 952x415x1333 | 952x415x1333 | 952x415x1333
Packing (WxDxH) | mm | 1095x495x1480 | 1095x495x1480 | 1095x495x1480
INDOOR UNIT |  | 42QTD048R8S | 42QZL048R8S | 42QSS048R8S
Indoor fan motor input | W | 141 | 96*2 | 560
Indoor fan motor max current | A | 0.45 | 0.85*2 | 4.1
Sound power level | dB(A) | 67 | 69 | 71
Sound pressure level (high/med/low) | dB(A) | 52/50/49 | 54/50/46 | 51/50/48
Air flow (high/med/low) | m3/h | 1720 / 1570 / 1380 | 2330 / 1930 / 1420 | 2400 / 2040 / 1680
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 29.0 / 33.0 | 41.2 / 47.6 | 47.5 / 56.0
Weight (Net/Gross)(Panel) | kg | 6.0 / 9.0 | / | /
Dimensions (WxDxH)(Body) | mm | 840×840×287 | 1650x675x235 | 1200x874x300
Packing (WxDxH)(Body) | mm | 900×900×307 | 1725x755x318 | 1405x915x365
Dimensions (WxDxH)(Panel) | mm | 950×950×55 | / | /
Packing (WxDxH)(Panel) | mm | 1035×1035×90 | / | /
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency

## 60K(3Ph)
Specification of LC 60K(R410A) (3 phase)
SYSTEM |  | Cassette 60K | Under-ceiling 60K | Ducted 60K
Cooling capacity | kW | 15.1 (5.0~16.0) | 15.5 (5.4~16.0) | 15.4 (5.2~16.0)
Heating capacity | kW | 18.0 (3.9~18.2) | 17.5 (4.3~18.5) | 17.6 (4.8~18.8)
Heating capacity at -7℃ | kW | 12.2 | 11.5 | 12.6
Heating capacity at -10℃ | kW | 11.9 | 11.1 | 11.8
Heating capacity at -15℃ | kW | 9.8 | 9.9 | 10.2
P design capacity cooling | kW | 15.1 | 15.5 | 15.4
P design capacity heating(average) | kW | 11.2 | 11.8 | 12
P design capacity heating(warmer) | kW | 12.1 | 11.6 | 12.2
SEER/SCOP(average)/SCOP(warmer) | W/W | 5.7 / 4.0 / 5.2 | 5.8 / 4.1 / 5.1 | 5.6 / 4.0 / 5.1
Energy label |  | A+ / A+ / A+++ | A+ / A+ / A+++ | A+ / A+ / A+++
Yearly energy consumption | kWh | 929/3916/3225 | 938/4011/3173 | 963/4196/3328
EER/COP | W/W | 2.4/3.1 | 2.5/3.1 | 2.3/3.4
Standard current (cooling) | A | 10.6 | 10.5 | 11
Standard input (cooling) | W | 6240 | 6150 | 6630
Standard current (heating) | A | 9.5 | 9.4 | 8.6
Standard input (heating) | W | 5760 | 5600 | 5140
OUTDOOR UNIT |  | 38QUS060DT-1
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage / Hz / Ph |  | 380~415V / 50Hz / 3Ph
Rated current | A | 14
Rated input | W | 7500
Refrigerant amount | kg | 4.3
Compressor model |  | ATQ420D1UMU
Refrigerant oil / oil quantity | ml | ESTER OIL VG74 / 1400
Liquid side/ Gas side | mm(inch) | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8") | Φ9.52/Φ15.9 (3/8"/5/8")
Standard piping length | m | 5 | 5 | 5
Min piping length | m | 3 | 3 | 3
Max piping length | m | 65 | 20 | 20
Max difference | m | 30 | 8 | 8
Additional charge | g/m | 30 | 15 | 15
Sound power level | dB(A) | 77
Sound pressure level | dB(A) | 64
Airflow | m3/h | 7000
Weight (Net/Gross) | kg | 112.8/126
Dimensions (WxDxH) | mm | 952x415x1333 | 952x415x1333 | 952x415x1333
Packing (WxDxH) | mm | 1095x495x1480 | 1095x495x1480 | 1095x495x1480
INDOOR UNIT |  | 42QTD060R8S | 42QZL060R8S | 42QSS060R8S
Indoor fan motor input | W | 232 | 90*2 | 560
Indoor fan motor max current | A | 1.92 | 0.75*2 | 4.1
Sound power level | dB(A) | 70 | 73 | 76
Sound pressure level (high/med/low) | dB(A) | 53 / 50 / 48 | 54 / 47 / 43 | 54 / 52 / 50
Air flow (high/med/low) | m3/h | 1970 / 1740 / 1540 | 2450 / 1830 / 1430 | 2600 / 2210 / 1820
External static pressure | Pa | 0 | 0 | 0~160
Weight (Net/Gross)(Body) | kg | 29.0 / 33.0 | 41.4 / 47.8 | 46.0 / 55.5
Weight (Net/Gross)(Panel) | kg | 6.0 / 9.0 | - | -
Dimensions (WxDxH)(Body) | mm | 840×840×287 | 1650×675×235 | 1200×874×300
Packing (WxDxH)(Body) | mm | 900×900×307 | 1725×755×318 | 1405×915×365
Dimensions (WxDxH)(Panel) | mm | 950×950×55 | - | -
Packing (WxDxH)(Panel) | mm | 1035×1035×90 | - | -
Note
* Sound data @ cooling mode
*-7℃/-10℃/-15℃ heating @ free frequency