## 18K-R8S (hidden)
Specification of LC（R32） 18K
SYSTEM |  | Cassette 18K | Under-ceiling 18K | Ducted 18K
Cooling capacity | kW | 5.20(2.60~5.70) | 5.20(2.60~5.60) | 5.20(2.80~5.50)
Heating capacity | kW | 5.50(2.30~5.80) | 5.70(2.30~5.80) | 5.50(2.40~5.80)
Heating capacity at -7℃ | kW | 3.9 | 4.3 | 4
Heating capacity at -10℃ | kW | 3.9 | 3.9 | 3.6
Heating capacity at -15℃ | kW | 2.2 | 3.2 | 2.5
Pdesign capacity cooling | kW | 5.2 | 5.2 | 5.2
Pdesign capacity heating (average) | kW | 4.7 | 4.7 | 4.7
Pdesign capacity heating (warmer) | kW | 4.7 | 4.7 | 4.7
SEER/SCOP(average)/SCOP(warmer) | W/W | 6.9 / 4.0 / 5.1 | 6.9 / 4.0 / 5.1 | 6.3 / 4.0 / 4.9
Energy label | - | A++ / A+ / A+++ | A++ / A+ / A+++ | A++ / A+ / A++
Yearly energy consumption | kWh | 264 / 1645 / 1290 | 264 / 1645 / 1290 | 289 / 1645 / 1343
EER/COP | W/W | 3.34 / 3.74 | 3.06 / 3.77 | 3.06 / 3.74
Standard current (cooling) | A | 7.7 | 7.7 | 7.7
Standard input (cooling) | W | 1700 | 1700 | 1700
Standard current (heating) | A | 6.8 | 6.8 | 6.8
Standard input (heating) | W | 1500 | 1500 | 1500
OUTDOOR UNIT |  | 38QUS018R8S
Temp range cooling | ℃ | -15~50
Temp range heating | ℃ | -15~24
Voltage/Hz/Ph | - | 220~240V / 50Hz / 1Ph
Rated current | A | 10
Rated input | W | 2200
Refrigerant amount (R32) | kg | 1.35
Compressor model | - | KSM135D23UFZ
Refrigerant oil/Oil quantity | ml | VG74 / 450
Liquid side/Gas side | mm(inch) | Φ6.35 / Φ12.7 (1/4" / 1/2")
Standard piping length | m | 5
Min piping length | m | 3
Max piping length | m | 30
Max difference | m | 20
Additional charge | g/m | 12
Sound power level | dB(A) | 65
Sound pressure level | dB(A) | 57
Airflow | m3/h | 2100
Weight (Net/Gross) | kg | 35.5 / 38.5
Dimensions (W×D×H) | mm | 800×333×554
Packing (W×D×H) | mm | 920×390×615
INDOOR UNIT |  | 42QTD018R8S | 42QZL018R8S | 42QSS018R8S
Indoor fan motor input | W | 58 | 100 | 90
Indoor fan motor max current | A | 0.332 | 1.11 | 1.2
Sound power level | dB(A) | 57 | 57 | 60
Sound pressure level (high/med/low) | dB(A) | 45 / 40 / 37 | 45 / 40 / 37 | 42 / 40 / 38
Air flow (high/med/low) | m3/h | 1040 / 870 / 760 | 900 / 790 / 680 | 1000 / 850 / 680
External static pressure | Pa | 0 | 0 | 0~100
Weight (Net/Gross)(Body) | kg | 21.5 / 25.0 | 27.0 / 32.0 | 25.5 / 31.5
Weight (Net/Gross)(Panel) | kg | 6.0 / 9.0 | - | -
Dimensions (W×D×H)(Body) | mm | 840×840×205 | 1068×675×235 | 880×674×210
Packing (W×D×H)(Body) | mm | 900×900×217 | 1145×755×313 | 1070×725×270
Dimensions (W×D×H)(Panel) | mm | 950×950×55 | - | -
Packing (W×D×H)(Panel) | mm | 1035×1035×90 | - | -
Note
* Sound data @ cooling mode
* -7℃/-10℃/-15℃ heating capacity @ free frequency
*42QTD018R8S had been phased out at June, 2018.
*38QUS018R8S had been phased out at June, 2019.

## 48K(3Ph)
Specification of LC（R32） 48K(3 phase)
SYSTEM |  | GD Floor standing 48K Will phase out in Oct,2021 | New GD Floor standing 48K
Cooling capacity | kW | 14.60（4.95~15.45） | 14.60（3.50~15.68）
Heating capacity | kW | 16.10（4.40~18.50） | 16.10（4.10~18.50）
Heating capacity at -7℃ | kW | 13.4 | 14.8
Heating capacity at -10℃ | kW | 11.3 | 11.35
Heating capacity at -15℃ | kW | 10 | 10
Pdesign capacity cooling | kW | 14.6 | 14.6
Pdesign capacity heating (average) | kW | 11 | 11
Pdesign capacity heating (warmer) | kW | 11.8 | 11
SEER/SCOP(average)/SCOP(warmer) | W/W | 6.1/4.0/5.1 | 6.2/4.0/5.1
Energy label | - | A++ / A+ / A+++ | A++ / A+ / A+++
Yearly energy consumption | kWh | 838/3850/3239 | 825/3850/3019
EER/COP | W/W | 2.81/3.10 | 2.95/3.74
Standard current (cooling) | A | 8 | 8
Standard input (cooling) | W | 5195 | 4950
Standard current (heating) | A | 8.5 | 7
Standard input (heating) | W | 5200 | 4300
OUTDOOR UNIT |  | 38QUS048R8T | 38QUS048D8T
Temp range cooling | ℃ | -15~50 | -15~50
Temp range heating | ℃ | -15~24 | -15~24
Voltage/Hz/Ph | - | 380~415V / 50Hz / 3Ph | 380~415V / 50Hz / 3Ph
Rated current | A | 11.2 | 13
Rated input | W | 6200 | 6900
Refrigerant amount (R32) | kg/TCO2 | 2.80/1.890 | 2.9/1.958 | revised
Compressor model | - | KTQ420D1UMU | KTQ420D1UMU
Refrigerant oil/Oil quantity | ml | VG74 / 1400 | VG74 / 1400
Liquid side/Gas side | mm(inch) | Φ9.52 / Φ15.9 (3/8" / 5/8") | Φ9.52 / Φ15.9 (3/8" / 5/8")
Standard piping length | m | 5 | 5
Min piping length | m | 3 | 3
Max piping length | m | 65 | 65
Max difference | m | 30 | 30
Additional charge | g/m | 24 | 24
Sound power level | dB(A) | 75 | 75 | revised
Sound pressure level | dB(A) | 66 | 63.5 | revised
Sound pressure level(Rated Frequency at Cooling Mode) | dB(A) | 61 | /
Airflow | m3/h | 7500 | 7500
Weight (Net/Gross) | kg | 107.0 / 120.0 | 103.7/118.3
Dimensions (W×D×H) | mm | 952×415×1333 | 952x415x1333
Packing (W×D×H) | mm | 1095×495×1480 | 1095x495x1480
INDOOR UNIT |  | 42QFD048R8S | 42QFD048D8S
Indoor fan motor input | W | 210 | 210
Indoor fan motor max current | A | 1.77 | 1.77
Sound power level | dB(A) | 66 | 66
Sound pressure level (high/med/low) | dB(A) | 55/53/51.5 | 53/49/47
Air flow (high/med/low) | m3/h | 2413/2222/2027 | 2413/2222/2027
External static pressure | Pa | 0 | 0
Weight (Net/Gross)(Body) | kg | 58.4 / 77.1 | 59.0/77.0
Weight (Net/Gross)(Panel) | kg | - | -
Dimensions (W×D×H)(Body) | mm | 629x456x1935 | 629x456x1935 | revised
Packing (W×D×H)(Body) | mm | 750x575x2055 | 750x575x2055 | revised
Dimensions (W×D×H)(Panel) | mm | - | -
Packing (W×D×H)(Panel) | mm | - | -
Note
* Sound data @ cooling mode
* -7℃/-10℃/-15℃ heating capacity @ free frequency