## Slide 1
New Engineering Mode

## Slide 2
Contents
General Information
>>
01
Running Data Checking
>>
02
Parameter Setting
>>
03

## Slide 3
General Information Running Data Checking Parameter Setting
Introduction Operation Instructions
Brief Features
Easier Operation
Combined “Data Checking” and “Presetting” functions
Easier data reading in “Data Checking” mode
More parameters for choosing in “Presetting” mode
RG10 G series
RG10P(G)
QHP models
RG10L(G)
QHE models

## Slide 4
Available Products Lines
General Information Running Data Checking Parameter Setting
Introduction Operation Instructions
Oasis Plus

## Slide 5
Introduction Operation Instructions
General Operation
General Information Running Data Checking Parameter Setting
Normal
Data Checking
Presetting
Or nothing in 60s
Nothing in 60s
+ 7s
+ 2s
2s
2s

## Slide 6
Operation Instructions Data Explanation
Into Data Checking mode
Press and hold “Power” and “Fan” buttons for 7 seconds
1
2
1
2
Press “Up” or “Down” to check different data
General Information Running Data Checking Parameter Setting
1
2

## Slide 7
Operation Instructions Data Explanation
Running Data Checking
General Information Running Data Checking Parameter Setting
Press “Up” or “Down” to choose different channel (CH, from 0-30) on the remote controller, then the indoor unit will show different data.
Channel
Data

## Slide 8
Data Checking List
CH | Code | Meaning | Remark | CH | Code | Meaning | Remark
0 |  | Detailed error code (nA if no error) |  | 16 | TT | Set temperature including compensation | Actual data, ℃
1 | T1 | Room temperature | Actual data, ℃ | 17 | nA | Reserved | 
2 | T2 | Indoor coil temperature | Actual data, ℃ | 18 | nA | Reserved | 
3 | T3 | Outdoor coil temperature | Actual data, ℃ | 19 | nA | Reserved | 
4 | T4 | Ambient temperature | Actual data, ℃ | 20 | oT | Target Frequency calculated by indoor | Without limitation
5 | TP | Discharge temperature | Actual data, ℃ | 21 | nA | Reserved | 
6 | FT | Targeted frequency | Actual data | 22 | nA | Reserved | 
7 | Fr | Actual frequency | Actual data | 23 | nA | Reserved | 
8 | dL | Running current | 3.2A=3 | 24 | nA | Reserved | 
9 | Uo | Input voltage | 220V=22* | 25 | nA | Reserved | 
10 | Sn | Reserved |  | 26 | nA | Reserved | 
11 | -- | Reserved |  | 27 | nA | Reserved | 
12 | Pr | Outdoor fan speed | Actual data/8 | 28 | nA | Reserved | 
13 | Lr | EXV opening steps | Actual data/8 | 29 | nA | Reserved | 
14 | Ir | Indoor fan speed | Actual data/8 | 30 | nA | Reserved | 
15 | Hu | Humidity (if a sensor there) | Actual data, % |  |  |  | 
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting
The indoor unit will show code for 2 seconds, and then the value.
* Some other units will show 22-20, some will show 20.

## Slide 9
Items Shown
TP
FT, Fr, oT
ir
T2
T1
T4
Pr
T3
Lr
Indoor Unit
Outdoor Unit
Design Parameters for reference
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting
T1
T2
T3
T4
TP

## Slide 10
Detailed Error Code (2 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
P10 | Low DC voltage protection | Outdoor PCB or IPM board | P1
P11 | High DC voltage protection | Outdoor PCB or IPM board | P1
P40 | Communication error between main control trip and drive chip | Outdoor PCB or IPM board | P4
P41 | Error of current sampling circuit of compressor | Outdoor PCB or IPM board | P4
P42 | Error of compressor start up | Compressor | P4
P43 | Phase lose protection | Connection cable of compressor | P4
P44 | Zero speed protection | Compressor | P4
P45 | Synchronization error between 341 chip and PWM | Outdoor PCB or IPM board | P4
P46 | Compressor speed out of control | Outdoor PCB or IPM board, or compressor | P4
P49 | Over current of compressor | Outdoor PCB or IPM board, compressor or refrigeration system | P4
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting

## Slide 11
Detailed Error Code (4 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
EH 31 | DC voltage is too low of indoor DC fan motor (with DC fan driver board) | Indoor PCB or DC fan driver board | EH 03
EH 32 | DC voltage is too high of indoor DC fan motor (with DC fan driver board) | Indoor PCB or DC fan driver board | EH 03
EH 33 | Over-current protection of indoor DC fan motor (with DC fan driver board) | Indoor PCB, DC fan driver board or indoor DC motor | EH 03
EH 34 | IPM protection of indoor DC fan motor (with DC fan driver board) | DC fan driver board or indoor DC motor | EH 03
EH 35 | Phase lack protection of indoor DC fan motor (with DC fan driver board) | Connection cable of indoor DC motor | EH 03
EH 36 | Current checking circuit faulty of indoor DC fan motor (with DC fan driver board) | DC fan driver board | EH 03
EH 37 | Zero speed protection of indoor DC fan motor (with DC fan driver board) | Indoor DC motor | EH 03
EC 55 | IPM temperature sensor open circuit or short circuit | IPM temperature sensor | EC 02
EC 71 | Over-current protection of outdoor DC fan motor | Outdoor PCB or DC motor | EC 07
EC 72 | Phase lack protection of outdoor DC fan motor | Connection cable of outdoor DC motor | EC 07
EC 73 | Zero speed protection of outdoor DC fan motor | Outdoor DC motor | EC 07
EC 74 | Current checking circuit faulty of outdoor DC fan motor | Outdoor PCB | EC 07
EC 75 | IPM protection of outdoor DC fan motor | Outdoor PCB or DC motor | EC 07
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting

## Slide 12
Detailed Error Code (4 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
EH b5 | Communication error between indoor PCB and smart eye | Indoor PCB or smart eye | EH 03
EH 0F | Smart eye fault | Smart eye | EH 03
EH 0L | Display EEPROM fault | Display board | EH 0b
PC 10 | Outdoor AC voltage is too low | Power supply or outdoor PCB | PC 01
PC 11 | Outdoor DC voltage is too high | Power supply or outdoor PCB | PC 01
PC 12 | Outdoor DC voltage is too low (MCE faulty of IR341 chip) | Power supply or outdoor PCB (Outdoor PCB) | PC 01
PC 40 | Communication error between main control trip and drive chip | Outdoor PCB or IPM board | PC 04
PC 41 | Error of current sampling circuit of compressor | Outdoor PCB or IPM board | PC 04
PC 42 | Error of compressor start up | Compressor | PC 04
PC 43 | Phase lose protection | Connection cable of compressor | PC 04
PC 44 | Zero speed protection | Compressor | PC 04
PC 45 | Suddenly power lost | Power wire looses connection | PC 04
PC 46 | Compressor speed out of control | Outdoor PCB or IPM board, or compressor | PC 04
PC 49 | Over current of compressor | Outdoor PCB or IPM board, compressor or refrigeration system | PC 04
PC 06 | High discharge temperature protection of compressor | Lack of refrigerant, blocked condenser (cooling) or blocked evaporator (heating) | 
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting

## Slide 13
Detailed Error Code (4 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
PC 08 | Over current of outdoor unit | Power supply, outdoor PCB or blocked refrigeration system | 
PH 09 | Indoor fan stop because of anti-cold wind function | Lack of refrigerant or blocked refrigeration system | 
PC 0F | IGBT fault of PFC circuit | Outdoor PCB | 
PH 90 | Hi evaporator temperature protection in heating mode | Blocked evaporator or capillary, EXV, or faulty sensor | 
PH 91 | Lo evaporator temperature protection in cooling mode | Lack of refrigerant or partial blocked capillary, EXV, or faulty sensor | 
PC 0A | Hi condenser temperature protection in cooling mode | Blocked condenser or capillary, EXV, or faulty sensor | 
LH 00 | Frequency limitation caused by high or low evaporator temperature |  | 
LC 01 | Frequency limitation caused by high condenser temperature |  | 
LC 02 | Frequency limitation caused by high discharge temperature |  | 
LC 03 | Frequency limitation caused by high current |  | 
LC 05 | Frequency limitation caused by high or low voltage |  | 
LC 06 | Frequency limitation caused by high IPM temperature or faulty PFC |  | 
LC 30 | Frequency limitation caused by high pressure |  | 
LC 31 | Frequency limitation caused by low pressure |  | 
LH 07 | Frequency limitation caused remote controller |  | 
Operation Instructions Data Explanation
General Information Running Data Checking Parameter Setting

## Slide 14
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting
Pre-setting when installation
With this mode, you can change some pre-settings such as auto-restart, temperature compensation and so on when installing an air conditioner to make it run more properly for real applications.
Note:
Presetting mode is only valid in 1 minutes when AC unit is first-time electrified.
The AC unit should be off.

## Slide 15
Into Parameter Setting
Note:
The remote controller should be in data checking mode first.
Press and hold “Power” button for 2 seconds to active presetting function in the channel.
2s
2s
Data Checking
Presetting
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting

## Slide 16
Parameter query
Press and hold “Power” button for 2 seconds
1
2
Press “OK” to query current parameter while the remote controller shows “CH”. The parameter will be shown on the indoor unit.
2
3
1
1
Press “Up” or “Down” button to choose a channel that you want to query
3
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting

## Slide 17
Query Example
Press and hold “Power” button for 2 seconds
1
2
Press “OK” to query current parameter while the remote controller shows “CH”. The parameter will be shown on the indoor unit.
(“6” means the fan will be off for 15 mins and run for 1 min.)
Press “Up” or “Down” button to choose channel 4 (Fan control when Ts reached)
3
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting

## Slide 18
Parameter setting
Press and hold “Power” button for 2 seconds
2
3
Press “Up” or “Down” to choose the suitable parameter.
2
3
3
4
4
Press “OK” to send the parameter to indoor unit.
The indoor unit will show the parameter sent by the controller to confirm acceptance, and then it will show “88”, which means the program is resetting.
1
Press “Up” or “Down” button to choose a channel that you want to set
1
1
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting

## Slide 19
For Example
The indoor unit will show “3” to confirm acceptance. And then it will show “88”, which means the program is resetting.
Press and hold “Power” button for 2 seconds
2
3
Press “Up” or “Down” to choose 3 (keep in setting fan speed).
4
Press “OK” to send the parameter to indoor unit.
1
Press “Up” or “Down” button to choose channel 4 (Fan control when Ts reached)
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting

## Slide 20
Settable Parameter List
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting
CH | Item | Parameter Meaning | Remark
0 | / | Nothing to set | 
1 | Auto-restart function | 0 – Inactive 1 – Active | 
2 | Heating temperature compensation | -6.5, -6.0, -5.5, …, 0.5, 1.0, 1.5, …, 7.0, 7.5, -- (Cancel) | 
3 | / | Nothing to set | 
4 | Fan control when Ts reached | 1 – Fan stop 2 – Fan runs at lowest RPM 3 – Fan runs at setting RPM 4 – Fan stops for 5 mins and runs for 1 mins 5 – Fan stops for 10 mins and runs for 1 mins 6 – Fan stops for 15 mins and runs for 1 mins 7 – Fan stops for 20 mins and runs for 1 mins 8 – Fan stops for 30 mins and runs for 1 mins 9 – Fan stops for 40 mins and runs for 1 mins 10 – Fan stops for 50 mins and runs for 1 mins 11 – Fan stops for 60 mins and runs for 1 mins | 

## Slide 21
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting
Settable Parameter List
CH | Item | Parameter Meaning | Remark
5 | / | Nothing to set | 
6 | Mode lock | CH – Cooling and heating (all modes) HH – Heating only (Heating + Fan only) CC – Cooling only (Cooling + Drying + Fan only) nU – Cooling and heating without Auto | Remote controller will change as well.
7 | Cooling temperature compensation | -3.0, -2.5, -2.0, …, 3.0, 3.5, -- (Cancel) | 
8 | / | Nothing to set | 
9 | / | Nothing to set | 
10 | / | Nothing to set | 
11 | Lowest setting temperature | 16-24 | Remote controller will change as well.
12 | Highest setting temperature | 25-30 | Remote controller will change as well.
13 | / | Nothing to set | 
14 | / | Nothing to set | 
15 | Mode priority selection for multi units | H – Heating first C – Cooling first | 

## Slide 22
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting
Settable Parameter List
CH | Item | Parameter Meaning | Remark
16 | / | Nothing to set | 
17 | / | Nothing to set | 
18 | Min. frequency limitation in cooling mode | 10, 11, 12, …, 49, 50, -- (Cancel) | 
19 | Min. frequency limitation in heating mode | 10, 11, 12, …, 49, 50, -- (Cancel) | 
20 | Max frequency selection in T4 limitation of Zone6 | 20, 21, 22, …, 149, 150, -- (Cancel) | 
21 | Frequency selection of outdoor forced-operation | 10, 11, 12, …, 249, 250, -- (Cancel) | 
22 | One button reset | rS – Reset | 
23 | Max. frequency selection in cooling mode | 40, 41, 42, …, 83, 84, -- (Cancel) | 
24 | Max. frequency selection in heating mode | 40, 41, 42, …, 83, 84, -- (Cancel) | 
25 | Cooling temperature compensation | -3.0, -2.5, -2.0, …, 3.0, 3.5, -- (Cancel) | 
26 | Heating temperature compensation | -6.5, -6.0, -5.5, …, 0.5, 1.0, 1.5, …, 7.0, 7.5, -- (Cancel) | 

## Slide 23
Operation Instructions Parameter Explanation
General Information Running Data Checking Parameter Setting
Settable Parameter List
CH | Item | Parameter Meaning | Remark
26 | Heating temperature compensation | -6.5, -6.0, -5.5, …, 0.5, 1.0, 1.5, …, 7.0, 7.5, -- (Cancel) | 
27 | Max. fan speed selection in cooling | -41, -40, -39, …, 19, 20, -- (Cancel) | Fan speed will add set data*8. It is risk. Do not set it if not necessary
28 | Min. fan speed selection in cooling | -41, -40, -39, …, 19, 20, -- (Cancel) | 
29 | Max. fan speed selection in heating | -41, -40, -39, …, 19, 20, -- (Cancel) | 
30 | Min. fan speed selection in heating | -41, -40, -39, …, 19, 20, -- (Cancel) | 
NOTE | Data in red is not valid for setting. |  |