## Spec for R32-18C
Specification of 18C high wall（R32）
OUTDOOR UNIT |  | 38QHG009D8SH | 38QHG012D8SH
Cool capacity | kW | 2.64 (1.03-3.22) | 3.36(1.38~4.31)
Heating capacity | kW | 2.85 (0.82-3.37) | 3.81(1.07~4.38)
P design capacity cooling | kW | 2.64 | 3.36
P design capacity heating(warmer) | kW | 2.5 | 2.6
P design capacity heating(average) | kW | 2.6 | 2.6
Temp range cooling | ℃ | -15~50 | -15~50
Temp range heating | ℃ | -15~24 | -15~24
SEER / SCOP(warmer) / SCOP(average) | W/W | 8.5 / 5.4 / 4.2 | 8.5 / 5.8 / 4.3
Energy label |  | A+++ / A+++ / A+ | A+++ / A+++ / A+
Yearly energy consumption | kWh | 109 / 648 / 867 | 138 / 628 / 846
EER/COP | W/W | 4.00 / 4.07 | 3.91 / 3.93
Voltage, Hz |  | 220-240V~, 50/60Hz | 220-240V~, 50/60Hz
Standard current (cooling) | A | 2.9 | 3.8
Standard input (cooling) | W | 660 | 860
Standard current (heating) | A | 3.1 | 4.4
Standard input (heating) | W | 700 | 1000
Rated current | A | 10 | 10
Rated input | W | 2150 | 2150
Refrigerant amount | kg | 0.62 | 0.62
Compressor model |  | KSN98D22UFZ | KSN98D22UFZ
Refrigerant oil/oil quantity | ml | ESTER OIL RB74AF 370 | ESTER OIL RB74AF 370
Liquid side/Gas side | mm(inch) | Φ6.35/Φ9.52 (1/4"/3/8") | Φ6.35/Φ9.52 (1/4"/3/8")
Standard piping length | m | 5 | 5
Min piping length | m | 3 | 3
Max piping length | m | 25 | 25
Max difference | m | 10 | 10
Additional charge | g/m | 12 | 12
INDOOR UNIT |  | 42QHG009D8SH | 42QHG012D8SH
Indoor fan motor Input | W | 20 | 20
Indoor fan motor max current | A | 0.5 | 0.5
Sound power level | dB(A) | 57 | 60
Sound pressure level (Min. ~ Max.) | dB(A) | 21~37 | 21~38
Air flow(Min. ~ Max.) | m3/h | 160~510 | 170~520
Weight (Net/Gross) | kg | 8.7/11.5 | 8.7/11.3
Dimensions (W×D×H) | mm | 835×208×295 | 835×208×295
Packing (W×D×H) | mm | 905×290×355 | 905×290×355
OUTDOOR UNIT |  | 38QHG009D8SH | 38QHG012D8SH
Sound power level | dB(A) | 61 | 65
Sound pressure level | dB(A) | 54 | 55
Airflow | m3/h | 2150 | 2200
Weight (Net/Gross) | kg | 26.2/28.8 | 26.4/28.8
Dimensions (W×D×H) | mm | 765×303×555 | 765×303×555
Packing (W×D×H) | mm | 887×337×610 | 887×337×610
Note
* Sound data @ cooling mode
* -7℃/-15℃/-20℃ heating @ free frequency