## Slide 1
EUROP LCAC change
May , 2021

## Slide 2
Product lines
Series | Picture | 12 | 18 | 24 | 30 | 36 (1phase) | 36 (3phase) | 42 | 48 (1phase) | 48 (3phase) | 60 (3 phase)
Compact Cassette |  | ● | ● |  |  |  |  |  |  |  | 
New Cassette |  |  |  | ● | ● | ● | ● | ● |  | ● | ●
Ceiling & Floor |  |  | ● | ● |  | ● | ● |  |  | ● | ●
A6 Duct |  | ● | ● | ● | ● | ● | ● | ● |  | ● | ●
Console |  | ● | ● |  |  |  |  |  |  |  | 
Floor&Standing |  |  |  |  |  |  |  |  | ● GD | ● GD | 

## Slide 3
Electrical difference
Features difference
Structure difference
Contents

## Slide 4
Electrical difference
●PCB function
● New refrigerant cool stream inverter technology
● Communication way

## Slide 5
Electrical difference
PCB standard function
-New cassette
 | Functions | Standard | Optional
Standard | Infrared WRC | Y | /
Standard | 2 WIRES WC | Y | /
Customized | 4 WIRES WC | N | Y
Standard | CCM WC | Y | Y
Standard | WIFI | Y | Y
Standard | ON-OFF | Y | Y
Standard | ALARM | Y | Y
 | Functions | Standard | Optional
NA | Infrared WRC | N | N
Customized | 2 WIRES WC | N | Y
Standard | 4 WIRES WC | Y | /
Standard | CCM WC | Y | Y
Standard | WIFI | Y | Y
Standard | ON-OFF | Y | Y
Standard | ALARM | Y | Y
New cassette
Super slim cassette
Note，
2 WIRES WC(2 core non-polarity Wired controller) and 4 WIRES WC(485 communication Wired controller) can not exist at same time.
Standard is 4 core wired controller
Port 120G2/120X2
Standard is 2 core wired controller
120G/120X port and 12B wired controller port

## Slide 6
Electrical difference
PCB function
- New Cassette
New Cassette Main control PCB | Wired controller port | Wifi port | Central control port
PCB1(standard) 24/30K 17122500004213 36~60K 17122500004211 | 120X(2core wired controller port | yes | yes
PCB2(optional) 24/30K 17122500A02909 36~60K 17122500A02907 | 120X2/120G2 (4core wired controller) port | yes | yes
Note，
TWINS and Central controller use same terminal X/Y/E, so these two functions you can just choose one

## Slide 7
Electrical difference
New Fan
2 core non-polarity Wired controller
Alarm
XYE/TWINS
ON-OFF
WIFI
CN41
CN8
CN33
CN3
CN23
CN38
PCB standard function
-New cassette

## Slide 8
Electrical difference
New cassette PCB
Super Slim cassette PCB
PCB standard function
-New cassette
2 core non-polarity Wired controller
CN41
CN38
WIFI
4 core CN40
Wired controller

## Slide 9
Electrical difference
WIFI connection
-New cassette wifi connection
①
②
③

## Slide 10
Electrical difference
WIFI connection
-New cassette wifi connection

## Slide 11
Electrical difference
PCB standard function
- New Duct and Under&Ceiling
 | Functions | Standard | Optional
Standard | Infrared WRC | Y | /
Customized | 2 WIRES WC | N | Y
Standard | 4 WIRES WC | Y | N
Standard | CCM WC | Y | /
Standard | WIFI | Y | N
Standard | ON-OFF | Y | /
Standard | ALARM | Y | /
New Duct and
Under&Ceiling
Old Duct and
Under&Ceiling
Note，
1.2 WIRES WC(2 core non-polarity Wired controller) and 4 WIRES WC(485 communication Wired controller) can not exist at same time.
2. 2 WIRES WC(2 core non-polarity Wired controller) +wifi and Central control(X,Y,E) can not exist at same time.
 | Functions | Standard | Optional
Standard | Infrared WRC | Y | /
Standard | 2 WIRES WC | Y | N
Customized | 4 WIRES WC | N | Y
Standard | CCM WC | Y | /
Customized | WIFI | N | Y
Standard | ON-OFF | Y | /
Standard | ALARM | Y | /

## Slide 12
Electrical difference
PCB function
- Duct and Under & Ceiling
New Duct and under&ceiling | Wired controller port | Wifi port | Central control port
PCB1(standard) | 120X(2core wired controller port | No | yes
PCB2(optional) | 120X(2core wired controller )port | yes | No
PCB3(optional) | 120X2/120G2 (4core wired controller) port | yes | yes
Note，
1. 2 WIRES WC(2 core non-polarity Wired controller) +wifi and TWINS and Central controller port all use the XYE terminal port so these three functions you can just choose one

## Slide 13
Electrical difference
PCB function
- Duct and Under & Ceiling
Series | Size | Standard main PCB1 board 120X(2core wired controller port | Optional main PCB2 board 120X(2core wired controller )port+Wifi Port | Optional main PCB3 board 120X2/120G2 (4core wired controller) port
R32 IDU New Under-ceiling | 18K-HP | 17122700001915 | 17122700A02648 | 17122700A02688
 | 24K-HP | 17122700001915 | 17122700A02648 | 17122700A02688
 | 36K-HP | 17122700001895 | 17122700A02647 | 17122700A02686
 | 48K-HP | 17122700001895 | 17122700A02647 | 17122700A02686
 | 60K-HP | 17122700001895 | 17122700A02647 | 17122700A02686
R32 IDU New Ducted | 12K-HP | 17123000007398 | 17123000A03227 | 17123000A03307
 | 18K-HP | 17123000007299 | 17123000A03225 | 17123000A03305
 | 24K-HP | 17123000007299 | 17123000A03225 | 17123000A03305
 | 30K-HP | 17123000007299 | 17123000A03225 | 17123000A03305
 | 36K-HP | 17123000007305 | 17123000A03245 | 17123000A03308
 | 42K-HP | 17123000007305 | 17123000A03245 | 17123000A03308
 | 48K-HP | 17123000007305 | 17123000A03245 | 17123000A03308
 | 60K-HP | 17123000007305 | 17123000A03245 | 17123000A03308

## Slide 14
Electrical difference
PCB1 standard function
- Duct and Under&Ceiling
CN23 ON-OFF
CN33 Alarm
CN9 XYE(Central controller)/TWINS
CN45 2 core non-polarity Wired controller
CN43 New Fan
PCB1 – standard 2 WIRES WC

## Slide 15
Electrical difference
PCB2 standard function
PCB2 - customize wifi port
CN23 ON-OFF
CN33 Alarm
CN49 Wifi
CN45 2 core non-polarity Wired controller
CN43 New Fan
- Duct and Under&Ceiling

## Slide 16
Electrical difference
PCB3 standard function
CN43 New Fan
CN23 ON-OFF
CN33 Alarm
CN9 XYE(Central controller)/TWINS
CN40 4 WIRES(485) WC/WIFI
PCB3 - customize 4 WIRES WC
- Duct and Under&Ceiling

## Slide 17
Electrical difference
New DUCT PCB
Old DUCT PCB
PCB standard function
- Duct and Under&Ceiling
Electrical Part for 2 core wired controller
CN45 2 core non-polarity Wired controller
CN40 4 core
Wired controller

## Slide 18
Electrical difference
WIFI connection
- DUCT and under&ceiling wifi connection
USB Connection
WiFi Module
Connection wire to LCAC product
Note , for DUCT and U&C type the original PCB don’t have wifi or CN40 terminal ， so it can not connect wifi module . If you want to connect wifi , you must customize .

## Slide 19
Electrical difference
PCB function
- Console
New Console
Old Console
Functions | Standard | Optional
Infrared WRC | N | N
2 WIRES WRC | N | N
4 WIRES WRC | Y | N
CCM WC | N | N
WIFI | N | N
ON-OFF | Y | N
ALARM | N | N
Functions | Standard | Optional
Infrared WRC | Y | N
2 WIRES WRC | N | N
4 WIRES WRC | N | Y
CCM WC | N | N
WIFI | N | N
ON-OFF | Y | N
ALARM | N | N
Connect to display board
Connect 120G1/120X1 WRC
Connect 12B WRC

## Slide 20
Electrical difference
PCB function
- Console
CN201 4 WIRES(485) WRC
Connect to 120G1/X1
CN23 ON-OFF

## Slide 21
Electrical difference
PCB function
- Console
Infrared WRC connection
Connect 485 WRC
Old display
New display
12B(5 core)
120G1/120X1(4 core)

## Slide 22
Electrical difference
New refrigerant cool stream inverter technology
old: Fan cool inverter technology
New: Refrigerant cool stream inverter technology

## Slide 23
Electrical difference
New refrigerant cool stream inverter technology

## Slide 24
Electrical difference
Communication way
New current loop: L/N/S/E
Same as RAC split and multi
Old: 485 communication: L1/N/E+S1/S2
Same as CAC products

## Slide 25
Electrical difference
Note，
Because of the communication way difference , new LCAC ERP and
Old LCAC ERP are not compatible .
New LCAC ERP IDU just match new LCAC ERP ODU.
Old LCAC ERP IDU just match Old LCAC ERP ODU.

## Slide 26
Structure difference
●Drainage Pump built out
● High Lift Water Pump
● Materials
● Fireproof and Anti-Rat E-box
● Bigger Air Outlet Dimension
● Bigger Evaporator
● Drainage Pipe Diameter
● Package
● Installation paperboard
● Panel

## Slide 27
Old Cassette | New Cassette
Key optimization： Water drainage pump is built-out. It takes only 10min to replace the pump, saving up to half an hour for the aftersales man. | 
Structure difference
New cassette
-Drainage Pump

## Slide 28
Key optimization： The lift of the water drainage pump increases from 750mm to 1000mm, water drainage capacity is higher. It’s convenient to install drainage piping under more space condition. | 
Structure difference
New cassette
1000mm
-High Lift Water Pump

## Slide 29
Old Cassette | New Cassette
Key optimization： The materials of the water collector is ABS, 2.4mm in thickness, more reliable comparing to previous 0.8mm absorbing-plastics molding type. | 
Structure difference
New cassette
-Materials
water collector :
0.8mm absorbing-plastics molding
water collector :
2.4mm ABS

## Slide 30
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： The electrical box are all-metal, and the dimension of the electrical outlet are designed Anti-Rat, preventing effectively the rats from entering in. | 
-Fireproof and Anti-Rat E-box

## Slide 31
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： The area of air outlet is 23% bigger than previous, air velocity and noise is lower. | 
-Bigger Air Outlet Dimension

## Slide 32
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： With optimized evaporator, heat exchange area and capacity is increased, and the air flow is improved. | 
-Bigger Evaporator

## Slide 33
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： The diameter of drainage pipe is changed from 32mm to the mainstream 25mm. | 
-Drainage Pipe Diameter

## Slide 34
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： Brand-new package design for the new cassette, real drop test height is bigger than previous. | 
-Package

## Slide 35
Structure difference
New cassette
Old Cassette | New Cassette
Key optimization： The installation paperboard must be customized with installation hook. | 
-Installation paperboard
Standard part
Customized part

## Slide 36
Structure difference
New cassette panel
Corner display
KJR-12B connection
Independent Vane Control
40CAS-L6
Note, KJR-12B can not control independent vane and Breezeless.

## Slide 37
Structure difference
New cassette panel
Corner display
KJR-12B connection
Independent Vane Control
T-MBQ4-04BD
Note，
KJR-12B can not control independent vane control ;
If you want to realize independent vane control , you must choose a special RC(RG67G1)) or 485WRC( KJR-120G/X, KJR-120G2/X2) .
RG67G1

## Slide 38
Structure difference
New cassette panel
Note，
New cassette panel and old cassette panel are not compatible
New cassette panel just match new cassette type
Old cassette panel just match super slim cassette type

## Slide 39
Features difference
Notes:* means optional, #means new functions for 18C.
New features
●1%~100%Grades Indoor Fan Speed
● Active clean
● Twins
● GA compressor frequency control
● X-ECO
● Gear
Below are old features, new LC also have below features

## Slide 40
Feature difference
1%~100%Grades Indoor Fan Speed
-New Features
Au
20%
40%
60%
100%
80%
Due to the DC fan motor, indoor fan speeds are 100 grades, more comfortable and energy saving.
Via remote controller to select fan speed first, then the controller will display fan speed percentage, you can use the “UP and Down” button to increase or decrease fan speed in 1% increments, to change into any percentage.

## Slide 41
Feature difference
Active clean
The active Clean Technology washes away dust, mold, and grease that may cause odors when it adheres to the heat exchanger by automatically freezing and then rapidly thawing the frost.
The internal wind wheel then keeps operating to blow-dry the evaporator, thus preventing the growth of mold and keeping the inside clean.
Step1：
Cool evap
Step3：
Evap defrost
and heat
Step2：
Evap frost
Step4：
Fan
-New Features

## Slide 42
Feature difference
Twins
Twins combination(Standard for some model)
The units can be installed as Twin systems: one outdoor unit can be connected with two indoor units. The indoor units can be combined in any of the different available ratings.
-New Features
 | IDU | Indoor | Outdoor
 | Type | Units | Unit
 | Duct | 12K + 12K | 24k
 | Duct | 18K + 18K | 36k
Twins | U&C |  | 
System | Duct | 24K + 24K | 48K
 | Cassette |  | 
 | U&C |  | 
 | Duct | 30K + 30K | 60K
 | Cassette |  | 

## Slide 43
Feature difference
Twins
Twins combination(Standard for some model)
-New Features
Note, TWINS and Central controller use same terminal X/Y/E, so these two functions you can just choose one .
with two indoor units. The indoor units can be combined in any of the different available ratings
MAIN
SLAVE

## Slide 44
Feature difference
Twins
Function combination table(include Twins)
-New Features
New cassette | 2 WIRES WC | 4 WIRES WC | Central controller | WIFI | TWINS | ONOFF | ALARM
Standard 1 | Y | N | Y | Y | N | Y | Y
Standard 2 | Y | N | N | Y | Y | Y | Y
Customized | N | Y | Y | Y | N | Y | Y
Customized | N | Y | N | Y | Y | Y | Y
DUCT/C&F | 2 WIRES WC | 4 WIRES WC | Central controller | Wifi | TWINS | ONOFF | ALARM
Standard 1 | Y | N | Y | N | N | Y | Y
Standard 2 | Y | N | N | N | Y | Y | Y
Customized | Y | N | N | Y | N | Y | Y
Customized | N | Y | Y | N | N | Y | Y
Customized | N | N | Y | Y | N | Y | Y
Customized | N | Y | N | N | Y | Y | Y
Customized | N | N | N | Y | Y | Y | Y
Customized | N | Y | Y | Y | N | Y | Y
Customized | N | Y | N | Y | Y | Y | Y

## Slide 45
Feature difference
GA compressor frequency control
The frequency of traditional air conditioner has dramatic fluctuation during operation, leading to the instability of room temperature. However, air conditioners break away from this pattern with our unique GA Stepless Comfort Technology（0.6Hz for every step）. Its inverter frequency variation is so smooth that you wouldn’t notice the room temperature fluctuation (± 0.5℃) at all.
Temperature Graph
GA Stepless Inverter Mode
Ordinary Inverter Mode
Fmax
Fmin
Fmax
Fmin
Ordinary Inverter Mode
GA Stepless Inverter Mode
±1℃
±0.5℃
-New Features

## Slide 46
Feature difference
X-ECO
X-ECO mode applies to inverter model, smart control on compressor frequency as low as 12HZ(depend on model). As a smart running mode, it limits the highest compressor frequency and fan speed of each stage by intelligent control system.
-New Features
X-ECO mode could energy save.

## Slide 47
Feature difference
Gear
728W
1038W
1295W
A++/A+ 9k model
-New Features
Carrier inverter air conditioners offer three operating power options: 50%, 75%, and 100%.
You can choose a lower power level to conserve energy.

## Slide 48
The end